## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM002_ver02.0
Reference Number: ID005
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | 1872 | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. Measured data is manually recorded by responsible staff for calculation of emission reduction. 2) Recorded data is checked its integrity once a month by responsible staff. The accuracy level of electric meter is ±0.5%. The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. - Calibration： Calibration was conducted by the Manufacturer at the time of Manufacturer's inspection. Next calibration is required after 10 years. | Continuously | Automatic collected data is also recorded and stored. Since the project period is 7 years, no calibration will be conducted during the project period.
| (2) | EIgrid,p | Electricity imported from the grid to the project site during the period p | 59813 | MWh/p | Option B | Invoice from the power company for Option B | [for Option B] Data is collected and recorded from invoices from the power company. | Every month
| (3) | hgen,p | Operating time of captive electricity generator during the period p | 0 | hours/p | Option C | Monitored data | Data is measured by meter equipped to a generator. | Continuously | In the project, there is no generator for captive electricity. Thus, this parameter is not applicable for this project.
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.843 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity |  | 0.8 | tCO2/MWh | CDM approved small scale methodology: AMS-I.A |  |  | In the project, there is no generator for captive electricity.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | 36.9 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | 14 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | 5.59 | - | Selected from the default values set in the methodology
| COPPJ,i | COP of project chiller i under the project specific conditions |  | 7.81 | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | 6.13 | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| RCgen | Rated capacity of generator |  | 0 | kW | Specification of generator for captive electricity
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 152 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM002_ver02.0
Reference Number: ID005
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 152.4458 | tCO2/p | ERp
2. Selected default values, etc.
| COP of reference chiller i under the standardizing temperature conditions |  |  |  | N/A | 5.59 | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 1730.5418 | tCO2/p | REp
|  | Reference emissions |  |  | N/A
|  |  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0.843 | tCO2/MWh | EFelec
|  |  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.8 | tCO2/MWh | EFelec
|  |  | Proportion of grid electricity over total electricity consumed at the project site |  | N/A | 1 | - | -
|  |  | Proportion of captive electricity over total electricity consumed at the project site |  | N/A | 0 | - | -
|  |  | Power consumption of project chiller i |  | Electricity | 1872 | MWh/p | ECPJ,i,p
|  |  | COP of reference chiller i under the standardizing temperature conditions |  | N/A | 5.59 | - | COPRE,i
|  |  | COP of project chiller i calculated under the standardizing temperature conditions |  | N/A | 6.13 | - | COPPJ,tc,i
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 1578.096 | tCO2/p | PEp
|  | Project emissions |  |  | N/A
|  |  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0.843 | tCO2/MWh | EFelec
|  |  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.8 | tCO2/MWh | EFelec
|  |  | Proportion of grid electricity over total electricity consumed at the project site |  | N/A | 1 | - | -
|  |  | Proportion of captive electricity over total electricity consumed at the project site |  | N/A | 0 | - | -
|  |  | Power consumption of project chiller i |  | Electricity | 1872 | MWh/p | ECPJ,i,p
[List of Default Values]
|  |  |  | COPRE,i (x<300USRt) | 4.92 | -
|  |  |  | COPRE,i (300≤x<450USRt) | 5.33 | -
|  |  |  | COPRE,i (450≤x<500USRt) | 5.59 | -
|  |  |  | COPRE,i (500≤x<700USRt) | 5.85 | -
|  |  |  | COPRE,i (700≤x<1250USRt) | 5.94 | -
|  |  |  | TDcooling | 1.5 | degree Celsius
|  |  |  | TDchilled | 1.5 | degree Celsius

## MSS
Monitoring Spreadsheet: JCM_ID_AM002_ver02.0
Reference Number: ID005
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Plant Manager | Responsible for project planning, implementation, monitoring results and reporting.
| Supervisor | Appointed to be in charge of confirming the archived data that are manually recorded / collected and provided by auto data collection system (the system) after being checked and corrected when necessary. Also, appointed to be in charge of monitoring procedure (data collection/storage and data sharing with manufacturer), including monitoring equipments and calibrations, and training of monitoring.
| Chiller Operator | Appointed to be in charge of manual data recording and direct checking of the archived data for irregularity and lack, in order for cross checking of data collected by the system.

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM002_ver02.0
Reference Number: ID005
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project chiller i during the period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments： 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording： 1) Measured data is automatically sent to a server where data is recorded and stored. Measured data is manually recorded by responsible staff for calculation of emission reduction. 2) Recorded data is checked its integrity once a month by responsible staff. The accuracy level of electric meter is ±0.5%. The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. - Calibration： Calibration was conducted by the Manufacturer at the time of Manufacturer's inspection. Next calibration is required after 10 years. | Continuously
|  | (2) | EIgrid,p | Electricity imported from the grid to the project site during the period p |  | MWh/p | Option B or Option C | Invoice from the power company for Option B or monitored data for Option C | [for Option B] Data is collected and recorded from invoices from the power company. | Every month
|  | (3) | hgen,p | Operating time of captive electricity generator during the period p |  | hours/p | Option C | Monitored data | Data is measured by meter equipped to a generator. | Continuously
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.843 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee.
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity |  | 0.8 | tCO2/MWh | CDM approved small scale methodology: AMS-I.A |  |  | In the project, there is no generator for captive electricity.
| Tcooling-out,i |  | Output cooling water temperature of project chiller i set under the project specific condition |  | 36.9 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| Tchilled-out,i |  | Output chilled water temperature of project chiller i set under the project specific condition |  | 14 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPRE,i |  | COP of reference chiller i under the standardizing temperature conditions |  | 5.59 | - | Selected from the default values set in the methodology
| COPPJ,i |  | COP of project chiller i under the project specific conditions |  | 7.81 | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPPJ,tc,i |  | COP of project chiller i calculated under the standardizing temperature conditions |  | 6.13 | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| RCgen |  | Rated capacity of generator |  | 0 | kW | Specification of generator for captive electricity
Table3: Ex-post estimation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | #DIV/0! |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM002_ver02.0
Reference Number: ID005
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | #DIV/0! | tCO2/p | ERp
2. Selected default values, etc.
| COP of reference chiller i under the standardizing temperature conditions |  |  |  | N/A | 5.59 | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | #DIV/0! | tCO2/p | REp
|  | Reference emissions |  |  | N/A
|  |  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0.843 | tCO2/MWh | EFelec
|  |  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.8 | tCO2/MWh | EFelec
|  |  | Proportion of grid electricity over total electricity consumed at the project site |  | N/A | #DIV/0! | - | -
|  |  | Proportion of captive electricity over total electricity consumed at the project site |  | N/A | #DIV/0! | - | -
|  |  | Power consumption of project chiller i |  | Electricity | 0 | MWh/p | ECPJ,i,p
|  |  | COP of reference chiller i under the standardizing temperature conditions |  | N/A | 5.59 | - | COPRE,i
|  |  | COP of project chiller i calculated under the standardizing temperature conditions |  | N/A | 6.13 | - | COPPJ,tc,i
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | #DIV/0! | tCO2/p | PEp
|  | Project emissions |  |  | N/A
|  |  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0.843 | tCO2/MWh | EFelec
|  |  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.8 | tCO2/MWh | EFelec
|  |  | Proportion of grid electricity over total electricity consumed at the project site |  | N/A | #DIV/0! | - | -
|  |  | Proportion of captive electricity over total electricity consumed at the project site |  | N/A | #DIV/0! | - | -
|  |  | Power consumption of project chiller i |  | Electricity | 0 | MWh/p | ECPJ,i,p
[List of Default Values]
|  |  |  | COPRE,i (x<300USRt) | 4.92 | -
|  |  |  | COPRE,i (300≤x<450USRt) | 5.33 | -
|  |  |  | COPRE,i (450≤x<500USRt) | 5.59 | -
|  |  |  | COPRE,i (500≤x<700USRt) | 5.85 | -
|  |  |  | COPRE,i (700≤x<1250USRt) | 5.94 | -
|  |  |  | TDcooling | 1.5 | degree Celsius
|  |  |  | TDchilled | 1.5 | degree Celsius