## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | EGi,j,p | Amount of electricity consumption by the facility j which is generated by the CGS i during the period p | - | MWh/p | Option C | Monitored data | Wattemeter is installed at the point(s) where the amount of electricity consumption by the facility which is generated by the CGS can be measured. A specification of wattemeter is provided by its manufacturer, and it states that the accuracy stays within ±2.5%. Therefore, a wattmeter is not a subject of calbration nor replacement in accordance with the manufacturer’s recommendation. | Continuously monitored and monthly aggregated | Values are input on "MPS(input_separate)" sheet.
| 2 | HGi,j,p | Amount of heat consumption by the facility j which is generated by the CGS i during the period p (Option 1) | - | GJ/p | Option C | Monitored data | Hot water flow meter, steam flow meter and thermometer are installed at the point(s) where the amount of heat consumption by the facility which is generated by the CGS can be measured. The amount of heat consumption is determined either by the following approach applying calculation results derived from a set of monitored data. The following formula is applied. HGi,j,p = Σt(VSTi,j,t × h × v-1 - VFWi,j,t × TIN,i,j,t × Cp × ρ) × 10-3 (for steam) HGi,j,p = Σt[VHWi,j,t × (TOUT,i,j,t - TIN,i,j,t)] × Cp × ρ × 10-3 (for hot water) Where: VSTi,j,t : Volume of steam consumption between time t-1 and t [m3] VFWi,j,t : Volume of feed water between time t-1 and t [m3] VHWi,j,t : Volume of hot water consumption between time t-1 and t [m3] TOUT,i,j,t : Outlet temperature of hot water at time t [K] TIN,i,j,t : Inlet temperature of feed water at time t [K] h : Specific enthalpy of steam [MJ/tonne] v : Specific volume of steam [m3/tonne] Cp : Specific heat capacity of water [MJ/tonne*K] ρ : Density of water [tonne/m3] t : Number of time period during the period p [-] Specifications of hot water flow meter, steam flow meter and thermometer are provided by the manufacturers, and the accuracy stays within ±2.0% for all type of meters. Therefore, hot water flow meter, steam flow meter and thermometer are not a subject of calbration nor replacement in accordance with the manufacturer’s recommendation. | Continuously monitored and monthly aggregated | Values are input on "MPS(input_separate)" sheet.
| 3 | HGSi,j,p | Amount of heat supply to the facility j which is generated by the CGS i during the period p (Option 2) | - | GJ/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of heat supply to the facility j which is generated by the CGS i can be measured. The amount of heat supply is determined by the approaches, as described for HGi,j,p above. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Monthly | Select the use of Option 2 in C30 of "MPS(input_separate)" sheet. If yes, values are input on "MPS(input_separate)" sheet.
| 4 | FCi,p | Amount of gas fuel consumption by the CGS i during the period p | - | Nm3/p | Option C or Option B | Monitored data or Invoice | Natural gas flowmeter is installed at the point(s) where the amount of gas fuel consumption by the CGS can be measured. Specifications of natural gas flowmeter is provided by the manufacturers, and it states that the accuracy stays within ±1.0%. However, natural gas flowmeter is to be replaced or calibrated in accordance with the government regulation. | Continuously monitored and monthly aggregated | Values are input on "MPS(input_separate)" sheet.
| na | DYSp | Number of days during the period p (Option 2) |  | day | Option C | Monitored data | Counting the number of days of a given monitoring period p | Once at the end of a given monitoring period p | Values are input, if Option 2 for HGi,j,p is selected.
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηRE | Reference boiler efficiency |  | 89 | % | Value derived from the result of survey. The default value, 89.0 [%], should be revised if necessary. |  |  | N/A
| NCVi | Net calorific value of gas fuel consumed by the CGS i |  | - | MJ/Nm3 | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFelec,RE,j | CO2 emission factor for consumed electricity in the facility j |  | - | tCO2/MWh | [Grid electricity] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [Captive electricity] CDM approved small scale methodology AMS-I.A. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFfuel,RE,j | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) |  | - | tCO2/GJ | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFfuel,PJ,i | CO2 emission factor for gas fuel consumed by the CGS i |  | - | tCO2/GJ | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Higher value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| HGCk | Heat generative capacity of the existing steam boiler k or hot water boiler k (Equivalent evaporation is used for steam boilers, and rated thermal output for hot water boilers.) |  | - | kg/h or kW | Catalogs, specifications prepared for the quotation or factory acceptance test data by manufacturer. |  |  | Values are input on "MPS(input_separate)" sheet, if Option 2 for HGi,j,p is selected.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 21793 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Plan Sheet (Input Separate Sheet) [Attachment to Project Design Document]
Table 4: Reference emissions for electricity consumption
| Parameters | Identification parameters |  | Parameters to be monitored ex post |  | Project-specific parameters to be fixed ex ante |  |  | Reference emissions for electricity consumption
|  | i | j | EGi,j,p |  | EFelec,RE,j |  |  | REelec,i,j,p
| Description of data | Identification number for the CGS | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Amount of electricity consumption by the facility j which is generated by the CGS i during the period p |  | CO2 emission factor for consumed electricity in the facility j |  |  | Reference emissions for electricity consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | MWh/p |  | tCO2/MWh |  |  | tCO2/p
| Estimated Values | 1 | 1 | 42163 |  | 0.877 |  |  | 36976.951
| Total | - | - | - |  | - |  |  | 36976.951
Table 5: Reference emissions for heat consumption (Option 1)
| Parameters | Identification parameters |  | Parameters to be monitored ex post |  | Project-specific parameters to be fixed ex ante |  |  | Reference emissions for heat consumption
|  | i | j | HGi,j,p |  | ηRE | EFfuel,RE,j |  | REheat,i,j,p
| Description of data | Identification number for the CGS | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Amount of heat consumption by the facility j which is generated by the CGS i during the period p |  | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) |  | Reference emissions for heat consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | GJ/p |  | % | tCO2/GJ |  | tCO2/p
| Estimated Values | 1 | 1 | 60846 |  | 89 | 0.0543 |  | 3712.2897
| Total | - | - | - |  | - | - |  | 3712.2897
Table 6: Reference emissions for heat consumption (Option 2)
| Use of Option 2: | No
| Parameters | Identification parameters |  |  |  | Maximum capacity |  |  | Parameters to be monitored ex post |  | Project-specific parameters to be fixed ex ante |  |  | Reference emissions for heat consumption
|  | j | i | k |  | HGk,j,p_hat | ƩHGk,j,p_hat |  | ƩHGSi,j,p | DYSp | ηRE | EFfuel,RE,j | HGCk | REheat,i,j,p
| Description of data | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Identification number for the CGS | Identification number for the existing boiler which supplies steam or hot water to the facility j | Boiler type | Maximum capacity of heat generation by the existing boiler k supplying to the facility j during the period p | Maximum capacity of heat generation by the existing boiler supplying to the facility j during the period p |  | Amount of heat supply to the facility j which is generated by the CGS(s) during the period p | Number of days during the period p | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) | Heat generative capacity of the existing steam boiler k or hot water boiler k | Reference emissions for heat consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | - | - | GJ/p | GJ/p | ≧ | GJ/p | day | % | tCO2/GJ | kg/h or kW | tCO2/p
| Units: Estimated Values; ≧: ≧ | 0 | 89
≧
≧
≧
≧
| Total | - | - | - | - | - | - | - | - | - | - | - | - | 0
Table 7: Project emissions
| Parameters | Identification parameters |  | Parameters to be monitored ex post |  | Project-specific parameters to be fixed ex ante |  | Project emissions
|  | i |  | FCi,p |  | NCVi | EFfuel,PJ,i | PEi,p
| Description of data | Identification number for the CGS |  | Amount of gas fuel consumption by the CGS i during the period p |  | Net calorific value of gas fuel consumed by the CGS i | CO2 emission factor for gas fuel consumed by the CGS i | Project emissions for CGS i during the period p
| Units | - |  | Nm3/p |  | MJ/Nm3 | tCO2/GJ | tCO2/p
| Estimated Values | 1 |  | 8904075 |  | 36.4 | 0.0583 | 18895.5156
| Total | - |  | - |  | - | - | 18895.5156

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 21793.725 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 40689.2407 | tCO2/p | REp
|  | Reference emissions for electricity consumption |  |  | N/A | 36976.951 | tCO2/p | ƩƩREelec,i,j,p
|  | Reference emissions for heat consumption |  |  | N/A | 3712.2897 | tCO2/p | ƩƩREheat,i,j,p
(Option 1 is selected)
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 18895.5156 | tCO2/p | PEp
[List of Default Values]
| ηRE |  | Reference boiler efficiency | 89 | %

## MSS
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Toyota Tsusho Corporation Industrial Machinery Department General Manager | In charge of authorizing the monitoring report.
| Toyota Tsusho Corporation Industrial Machinery Department Project Manager | In charge of approving the archived data after being checked and corrected when necessary and preparation of monitoring report.
| PT. Toyota Motor Manufacturing Indonesia Plant Engineering & SHE Division Utility & Building Operation Karawang General Manager | In charge of monitoring procedure (data collection and storage), including monitoring equipments and calibrations, and training of monitoring personnel.
| PT. Toyota Motor Manufacturing Indonesia Plant Engineering & SHE Division Utility & Building Operation Karawang Supervisor | In charge of checking the archived data.

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | 1 | EGi,j,p | Amount of electricity consumption by the facility j which is generated by the CGS i during the period p | - | MWh/p | Option C | Monitored data | Wattemeter is installed at the point(s) where the amount of electricity consumption by the facility which is generated by the CGS can be measured. A specification of wattemeter is provided by its manufacturer, and it states that the accuracy stays within ±2.5%. Therefore, a wattmeter is not a subject of calbration nor replacement in accordance with the manufacturer’s recommendation. | Continuously monitored and monthly aggregated | Values are input on "MRS(input_separate)" sheet.
|  | 2 | HGi,j,p | Amount of heat consumption by the facility j which is generated by the CGS i during the period p (Option 1) | - | GJ/p | Option C | Monitored data | Hot water flow meter, steam flow meter and thermometer are installed at the point(s) where the amount of heat consumption by the facility which is generated by the CGS can be measured. The amount of heat consumption is determined either by the following approach applying calculation results derived from a set of monitored data. The following formula is applied. HGi,j,p = Σt(VSTi,j,t × h × v-1 - VFWi,j,t × TIN,i,j,t × Cp × ρ) × 10-3 (for steam) HGi,j,p = Σt[VHWi,j,t × (TOUT,i,j,t - TIN,i,j,t)] × Cp × ρ × 10-3 (for hot water) Where: VSTi,j,t : Volume of steam consumption between time t-1 and t [m3] VFWi,j,t : Volume of feed water between time t-1 and t [m3] VHWi,j,t : Volume of hot water consumption between time t-1 and t [m3] TOUT,i,j,t : Outlet temperature of hot water at time t [K] TIN,i,j,t : Inlet temperature of feed water at time t [K] h : Specific enthalpy of steam [MJ/tonne] v : Specific volume of steam [m3/tonne] Cp : Specific heat capacity of water [MJ/tonne*K] ρ : Density of water [tonne/m3] t : Number of time period during the period p [-] Specifications of hot water flow meter, steam flow meter and thermometer are provided by the manufacturers, and the accuracy stays within ±2.0% for all type of meters. Therefore, hot water flow meter, steam flow meter and thermometer are not a subject of calbration nor replacement in accordance with the manufacturer’s recommendation. | Continuously monitored and monthly aggregated | Values are input on "MRS(input_separate)" sheet.
|  | 3 | HGSi,j,p | Amount of heat supply to the facility j which is generated by the CGS i during the period p (Option 2) | - | GJ/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of heat supply to the facility j which is generated by the CGS i can be measured. The amount of heat supply is determined by the approaches, as described for HGi,j,p above. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Monthly | Select the use of Option 2 in C30 of "MRS(input_separate)" sheet. If yes, values are input on "MRS(input_separate)" sheet.
|  | 4 | FCi,p | Amount of gas fuel consumption by the CGS i during the period p | - | Nm3/p | Option C or Option B | Monitored data or Invoice | Natural gas flowmeter is installed at the point(s) where the amount of gas fuel consumption by the CGS can be measured. Specifications of natural gas flowmeter is provided by the manufacturers, and it states that the accuracy stays within ±1.0%. However, natural gas flowmeter is to be replaced or calibrated in accordance with the government regulation. | Continuously monitored and monthly aggregated | Values are input on "MRS(input_separate)" sheet.
|  | na | DYSp | Number of days during the period p (Option 2) |  | day | Option C | Monitored data | Counting the number of days of a given monitoring period p | Once at the end of a given monitoring period p | Values are input, if Option 2 for HGi,j,p is selected.
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηRE |  | Reference boiler efficiency |  | 89 | % | Value derived from the result of survey. The default value, 89.0 [%], should be revised if necessary. |  |  | N/A
| NCVi |  | Net calorific value of gas fuel consumed by the CGS i |  | - | MJ/Nm3 | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFelec,RE,j |  | CO2 emission factor for consumed electricity in the facility j |  | - | tCO2/MWh | [Grid electricity] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [Captive electricity] CDM approved small scale methodology AMS-I.A. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFfuel,RE,j |  | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) |  | - | tCO2/GJ | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| EFfuel,PJ,i |  | CO2 emission factor for gas fuel consumed by the CGS i |  | - | tCO2/GJ | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Higher value is applied. |  |  | Values are input on "MPS(input_separate)" sheet.
| HGCk |  | Heat generative capacity of the existing steam boiler k or hot water boiler k (Equivalent evaporation is used for steam boilers, and rated thermal output for hot water boilers.) |  | - | kg/h or kW | Catalogs, specifications prepared for the quotation or factory acceptance test data by manufacturer. |  |  | Values are input on "MPS(input_separate)" sheet, if Option 2 for HGi,j,p is selected.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period | CO2 emission reductions |  | Units
|  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Report Sheet (Input Separate Sheet) [For Verification]
Table 4: Reference emissions for electricity consumption
| Parameters | Identification parameters |  | Parameters monitored ex post |  | Project-specific parameters fixed ex ante |  |  | Reference emissions for electricity consumption
|  | i | j | EGi,j,p |  | EFelec,RE,j |  |  | REelec,i,j,p
| Description of data | Identification number for the CGS | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Amount of electricity consumption by the facility j which is generated by the CGS i during the period p |  | CO2 emission factor for consumed electricity in the facility j |  |  | Reference emissions for electricity consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | MWh/p |  | tCO2/MWh |  |  | tCO2/p
| Estimated /Monitored Values | 1 | 1 |  |  | 0.877 |  |  | 0
| Total | - | - | - |  | - |  |  | 0
Table 5: Reference emissions for heat consumption (Option 1)
| Parameters | Identification parameters |  | Parameters monitored ex post |  | Project-specific parameters fixed ex ante |  |  | Reference emissions for heat consumption
|  | i | j | HGi,j,p |  | ηRE | EFfuel,RE,j |  | REheat,i,j,p
| Description of data | Identification number for the CGS | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Amount of heat consumption by the facility j which is generated by the CGS i during the period p |  | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) |  | Reference emissions for heat consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | GJ/p |  | % | tCO2/GJ |  | tCO2/p
| Estimated /Monitored Values | 1 | 1 |  |  | 89 | 0.0543 |  | 0
| Total | - | - | - |  | - | - |  | 0
Table 6: Reference emissions for heat consumption (Option 2)
| Use of Option 2: | No
| Parameters | Identification parameters |  |  |  | Maximum capacity |  |  | Parameters monitored ex post |  | Project-specific parameters fixed ex ante |  |  | Reference emissions for heat consumption
|  | j | i | k |  | HGk,j,p_hat | ƩHGk,j,p_hat |  | ƩHGSi,j,p | DYSp | ηRE | EFfuel,RE,j | HGCk | REheat,i,j,p
| Description of data | Identification number for the facility to which electricity and heat generated by the CGS i is supplied | Identification number for the CGS | Identification number for the existing boiler which supplies steam or hot water to the facility j | Boiler type | Maximum capacity of heat generation by the existing boiler k supplying to the facility j during the period p | Maximum capacity of heat generation by the existing boiler supplying to the facility j during the period p |  | Amount of heat supply to the facility j which is generated by the CGS(s) during the period p | Number of days during the period p | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler in the facility j (CO2 emission factor of natural gas is applied.) | Heat generative capacity of the existing steam boiler k or hot water boiler k | Reference emissions for heat consumption by the facility j which is generated by the CGS i during the period p
| Units | - | - | - | - | GJ/p | GJ/p | ≧ | GJ/p | day | % | tCO2/GJ | kg/h or kW | tCO2/p
| Units: Estimated /Monitored Values; ≧: ≧ | 0 | 89
≧
≧
≧
≧
| Total | - | - | - | - | - | - | - | - | - | - | - | - | 0
Table 7: Project emissions
| Parameters | Identification parameters |  | Parameters monitored ex post |  | Project-specific parameters fixed ex ante |  | Project emissions
|  | i |  | FCi,p |  | NCVi | EFfuel,PJ,i | PEi,p
| Description of data | Identification number for the CGS |  | Amount of gas fuel consumption by the CGS i during the period p |  | Net calorific value of gas fuel consumed by the CGS i | CO2 emission factor for gas fuel consumed by the CGS i | Project emissions for CGS i during the period p
| Units | - |  | Nm3/p |  | MJ/Nm3 | tCO2/GJ | tCO2/p
| Estimated /Monitored Values | 1 |  |  |  | 36.4 | 0.0583 | 0
| Total | - |  | - |  | - | - | 0

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM016_ver01.0
Reference Number: ID019
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions for electricity consumption |  |  | N/A | 0 | tCO2/p | ƩƩREelec,i,j,p
|  | Reference emissions for heat consumption |  |  | N/A | 0 | tCO2/p | ƩƩREheat,i,j,p
(Option 1 is selected)
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
| ηRE |  | Reference boiler efficiency | 89 | %