## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | CPJ,i,p | Cooling energy generated by project absorption chiller i during the period p |  | MWh/p | Option C | Monitored data | Data (chilled water temperature and flow rate) are measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. The monitored data will be archived electronically for two years after the final issuance of credits. To obtain the CPJ,i,p from those monitored data, following formula is applied: CPJ,i,p= ∑(water flow rate ×(Toutlet -Tinlet)×Cp×ρ×10-3× hOP,i ×0.2778) - Water flow rate: Quantity of chilled water generated by the project absorption chiller i per hour [m3/hour] - Tinlet : Inlet temperature of the feed water for chilled water to be generated by the project absorption chiller i per hour at operating hour h [degree Celsius] - Toutlet : Outlet temperature of the chilled water generated by the project absorption chiller i per hour [degree Celsius] - Cp : Specific heat capacity of water [MJ/tonne- degree Celsius] - ρ : Density of water [tonne /m3] - hOP,i : Operating hour of the project absorption chiller i | Continuously | Input on "MPS (input_separate)" Formula is from page I-5 of JCM ID_AM010_ver01.0.
| (2) | ECPJ,i,p | Electricity consumption by project absorption chiller i during the period p | - | MWh/p | Option C | Monitored data | Method I Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. Method II Value is calculated by multiplying the electric power (catalogue/specification value) by operation hours of the project chiller. This project uses Method II. | Continuously | Input on "MPS (input_separate)"
| (3) | FCPJ,i,p | Gas fuel consumption by project absorption chiller i during the period p | - | Nm3/p | Option B or C | Invoice or Monitored data | Method I Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. Method II Data on invoice provided by gas fuel supplier is used. | Continuously | N/A
| (4) | hOP,I,p | Operating hours of the project absorption chiller i during the period p | - | hours | Option C | Monitored data | This parameter is only used to calculate power consumption of project chiller (ECPJ,i,p) in Method II describe above. Data is measured by measuring equipment. Otherwise, "24 hours" may be applied in a conservative manner. | Continuously | Input on "MPS (input_separate)"
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor for consumed electricity |  | 0.877 | tCO2/MWh | [Grid electricity] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, Indonesia Joint Crediting Mechanism (JCM) website, based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [Captive electricity] CDM approved small scale methodology AMS-I.A.
| COPRE,i | COP of reference chiller i |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer. The default COP values are derived from the result of survey on COP of chillers from manufacturers that have high market share. The survey should prove the use of clear methodology. The default COP values should be revised if necessary from survey result which is conducted by JC or project participants. |  |  | Input on "MPS (input_separate)"
| NCVfuel,i | Net calorific value of gas fuel consumed by project absorption chiller i |  | - | MJ/Nm3 | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | N/A
| EFfuel,i | CO2 emission factor for gas fuel consumed by project absorption chiller i |  | - | tCO2/GJ | In order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Higher value is applied. |  |  | N/A
| EPPJ,i | Electric power of the project absorption chiller i |  | - | kW | Catalogue or specification of project chiller i prepared for the quotation or factory acceptance test data by manufacturer. (This parameter is only used to calculate power consumption of project chiller (ECPJ,i,p) in Method II describe above.) |  |  | Input on "MPS (input_separate)"
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 712 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Plan Sheet (Input Separate Sheet) [Attachment to Project Design Document]
| Identification number | Parameters to be monitored ex post |  |  |  | Project-specific parameters to be fixed ex ante |  |  |  |  | Ex-ante estimation of emissions
Parameters | i | CPJ,i,p | ECPJ,i,p | FCPJ,i,p | hOP,I,p | EFelec | COPRE,i | NCVfuel,i | EFfuel,i | EPPJ,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of the project absorption chiller | Cooling energy generated by project absorption chiller i during the period p | Electricity consumption by project absorption chiller i during the period p | Gas fuel consumption by project absorption chiller i during the period p | Operating hours of the project absorption chiller i during the period p | CO2 emission factor for consumed electricity | COP of reference chiller i | Net calorific value of gas fuel consumed by project absorption chiller i | CO2 emission factor for gas fuel consumed by project absorption chiller i | Electric power of the project absorption chiller i | Reference emissions of reference chiller i during the period p | Project emissions of project absorption chiller i during the period p | Emissions reductions by the project absorption chiller i during the period p
Units | - | MWh/p | MWh/p | Nm3/p | hours | tCO2/MWh | - | MJ/Nm3 | tCO2/GJ | kW | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 4983.264 |  |  | 4290 | 0.877 | 5.9 |  |  | 7.6 | 740.7326 | 28.5937 | 712.1389
| 2 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 3 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 4 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 5 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 6 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 7 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 8 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 9 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 10 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 11 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 12 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 13 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 14 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 15 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 16 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 17 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 18 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 19 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| 20 |  |  |  |  | 0.877 |  |  |  |  | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | 740.7326 | 28.5937 | 712.1389

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 712.1389 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 740.7326 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 740.7326 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 28.5937 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 28.5937 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (x≤350USRt) | 5.46 | -
|  |  | COPRE,i (350<x≤550USRt) | 5.69 | -
|  |  | COPRE,i (550<x≤750USRt) | 5.9 | -
|  |  | COPRE,i (750<x≤1,300USRt) | 6.03 | -

## MSS
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| JCM Project Manager (Tokyo Century Corporation) | - Responsible for preparation of a monitoring report
| Engineering Manager (PT. Timuraya Tunggal) | - Responsible for project planning, implementation, calibration of the monitoring equipments, monitoring results and reporting.
| Project Operators (PT. Timuraya Tunggal) | - Responsible for daily recording of monitoring data - Checking the data electronically transmitted and recorded via the monitoring system or based on manual recording when electronic recording is not available

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | CPJ,i,p | Cooling energy generated by project absorption chiller i during the period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously | Input on "MRS (input_separate)"
|  | (2) | ECPJ,i,p | Electricity consumption by project absorption chiller i during the period p | - | MWh/p | Option C | Monitored data | Method I Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. Method II Value is calculated by multiplying the electric power (catalogue/specification value) by operation hours of the project chiller. | Continuously | Input on "MRS (input_separate)"
|  | (3) | FCPJ,i,p | Gas fuel consumption by project absorption chiller i during the period p | - | Nm3/p | Option B or C | Invoice or Monitored data | Method I Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. Method II Data on invoice provided by gas fuel supplier is used. | Continuously | Input on "MRS (input_separate)"
|  | (4) | hOP,I,p | Operating hours of the project absorption chiller i during the period p | - | hours | Option C | Monitored data | This parameter is only used to calculate power consumption of project chiller (ECPJ,i,p) in Method II describe above. Data is measured by measuring equipment. QA/QC procedures as same as for measuring equipment of cooling output is applied. Otherwise, "24 hours" may be applied in a conservative manner. | Continuously | Input on "MRS (input_separate)"
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | CO2 emission factor for consumed electricity |  | 0.877 | tCO2/MWh | [Grid electricity] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, Indonesia Joint Crediting Mechanism (JCM) website, based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [Captive electricity] CDM approved small scale methodology AMS-I.A. |  |  | 0
| COPRE,i |  | COP of reference chiller i |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer. The default COP values are derived from the result of survey on COP of chillers from manufacturers that have high market share. The survey should prove the use of clear methodology. The default COP values should be revised if necessary from survey result which is conducted by JC or project participants. |  |  | Input on "MPS (input_separate)"
| NCVfuel,i |  | Net calorific value of gas fuel consumed by project absorption chiller i |  | - | MJ/Nm3 | In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | N/A
| EFfuel,i |  | CO2 emission factor for gas fuel consumed by project absorption chiller i |  | - | tCO2/GJ | In order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Higher value is applied. |  |  | N/A
| EPPJ,i |  | Electric power of the project absorption chiller i |  | - | kW | Catalogue or specification of project chiller i prepared for the quotation or factory acceptance test data by manufacturer. (This parameter is only used to calculate power consumption of project chiller (ECPJ,i,p) in Method II describe above.) |  |  | Input on "MPS (input_separate)"
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period | CO2 emission reductions |  | Units
|  | 0 |  | tCO2/p
[Monitoring option]
|  | Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
|  | Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
|  | Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Report Sheet (Input Separate Sheet) [For Verification]
| Identification number | Parameters monitored ex post |  |  |  | Project-specific parameters fixed ex ante |  |  |  |  | Ex-post calculation of emissions
Parameters | i | CPJ,i,p | ECPJ,i,p | FCPJ,i,p | hOP,I,p | EFelec | COPRE,i | NCVfuel,i | EFfuel,i | EPPJ,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of the project absorption chiller | Cooling energy generated by project absorption chiller i during the period p | Electricity consumption by project absorption chiller i during the period p | Gas fuel consumption by project absorption chiller i during the period p | Operating hours of the project absorption chiller i during the period p | CO2 emission factor for consumed electricity | COP of reference chiller i | Net calorific value of gas fuel consumed by project absorption chiller i | CO2 emission factor for gas fuel consumed by project absorption chiller i | Electric power of the project absorption chiller i | Reference emissions of reference chiller i during the period p | Project emissions of project absorption chiller i during the period p | Emissions reductions by the project absorption chiller i during the period p
Units | - | MWh/p | MWh/p | Nm3/p | hours | tCO2/MWh | - | MJ/Nm3 | tCO2/GJ | kW | tCO2/p | tCO2/p | tCO2/p
Monitored values | 1 |  |  |  |  | 0.877 | 5.9 | 0 | 0 | 7.6 | 0 | 0 | 0
| 2 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 |  |  |  |  | 0.877 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | 0 | 0 | 0

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM022_ver01.0
Reference Number: ID024
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (x≤350USRt) | 5.46 | -
|  |  | COPRE,i (350<x≤550USRt) | 5.69 | -
|  |  | COPRE,i (550<x≤750USRt) | 5.9 | -
|  |  | COPRE,i (750<x≤1,300USRt) | 6.03 | -