## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,p | Electricity consumption by the recipient facility i which is generated by the CGS during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MPS(input_separate)" sheet
| (2) | HCi,p | Heating energy consumption by the recipient facility i which is generated by the CGS during the period p | - | GJ/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of heating energy consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MPS(input_separate)" sheet
| (3) | CPJ,j,p | Cooling energy generated by the project absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of cooling energy consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MPS(input_separate)" sheet
| (4) | FCPJ,CGS,p | Gas fuel consumption by the CGS during the period p | 2641968 | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously
| (5) | ECPJ,CL,j,p | Electricity consumption by project absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. When project absorption chiller consumes electricity only generated by the project CGS, this parameter can be omitted or equal to zero (0), since CO2 emissions from electricity consumption by project absorption chiller are included in project emissions from the CGS. | Continuously | Input on "MPS(input_separate)" sheet
| (6) | FCPJ,CL,j,p | Gas fuel consumption by project absorption chiller j during the period p | - | Nm3/p | Option C | Monitored data | The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MPS(input_separate)" sheet
Table 1-annex: Parameters to be monitored ex post (in case of EFelec,i and or EFelec,j is calculated from measured data)
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (7) | FCcap,i,p | Amount of fuel consumed by the captive power generation system connected to the recipient facility i during the period p | - | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MPS(input_separate)" sheet
| (8) | EGcap,i,p | Amount of electricity generated by the captive power generation system connected to the recipient facility i during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity generated by the captive power generation system connected to the recipient facility i can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MPS(input_separate)" sheet
| (9) | FCcap,j,p | Amount of fuel consumed by the captive power generation system connected to the absorption chiller j during the period p | - | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MPS(input_separate)" sheet
| (10) | EGcap,j,p | Amount of electricity generated by the captive power generation system connected to the absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity generated by the captive power generation system connected to the absorption chiller j can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MPS(input_separate)" sheet
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηRE | Reference boiler efficiency |  | 89 | % | Value derived from the result of survey. The default value, 89 [%], should be revised if necessary.
| NCVfuel,CGS | Net calorific value of gas fuel consumed by the CGS |  | 0.03426 | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFfuel,RE | CO2 emission factor for fossil fuel consumed by the reference boiler (CO2 emission factor of natural gas is applied in this methodology) |  |  | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel,CGS | CO2 emission factor for gas fuel consumed by the CGS |  | 0.0583 | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFelec,i | [For grid electricity] CO2 emission factor for consumed electricity in the recipient facility i |  | - | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,i | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option a |  | - | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i. |  |  | Calculated
| EFelec,i | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option b |  | - | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated; Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i. |  |  | Calculated
| EFelec,i | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants. |  |  | Input on "MPS(input_separate)" sheet
| ηcap,i | Power generation efficiency of the captive power generation system connected to the recipient facility i |  | - | % | Specification of the captive power generation system connected to the recipient facility i, provided by the manufacturer. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,cap,i | Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,cap,i | CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| COPRE,j | COP of reference chiller j |  | - | dimensionless | Specifications of project chiller j prepared for the quotation or factory acceptance test data by manufacturer. The default COP values are derived from the result of survey on COP of chillers from manufacturers that have high market share. The survey should prove the use of clear methodology. The default COP values should be revised if necessary from survey result which is conducted by JC or project participants. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,j | [For grid electricity] CO2 emission factor for consumed electricity by the project absorption chiller j |  | - | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,j | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option a |  | - | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j. |  |  | Calculated
| EFelec,j | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option b |  | - | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated; Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j. |  |  | Calculated
| EFelec,j | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants. |  |  | Input on "MPS(input_separate)" sheet
| ηcap,j | Power generation efficiency of the captive power generation system connected to the project absorption chiller j |  | - | % | Specification of the captive power generation system connected to the project absorption chiller j, provided by the manufacturer. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,cap,j | Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,cap,j | CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,CL,j | Net calorific value of gas fuel consumed by the project absorption chiller j |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,CL,j | CO2 emission factor for gas fuel consumed by the project absorption chiller j |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 3863 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Plan Sheet (Input Separate Sheet) [Attachment to Project Design Document]
Table 4: Ex-ante estimation of reference emissions for electricity consumed by the recipient facility which is generated by the CGS
| parameters | Identification No. | Parameters to be monitored ex post | Parameters to be monitored ex post (in case of EFelec,i is calculated from measured data) |  | Project-specific parameters to be fixed ex ante | [6 empty] | Ex-ante estimation of reference emissions
|  | i | ECi,p | FCcap,i,p | EGcap,i,p | EFelec,i | EFelec,i | EFelec,i | EFelec,i | ηcap,i | NCVfuel,cap,i | EFfuel,cap,i | REelec,i,p
| Description of data | Identification number for the recipient facility to which electricity and heat generated by the CGS is supplied | Electricity consumption by the recipient facility i which is generated by the CGS during the period p | Amount of fuel consumed by the captive power generation system connected to the recipient facility i during the period p | Amount of electricity generated by the captive power generation system connected to the recipient facility i during the period p | [For grid electricity] CO2 emission factor for consumed electricity in the recipient facility i | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option a | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option b | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i | Power generation efficiency of the captive power generation system connected to the recipient facility i | Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i | CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i | Reference emissions for electricity consumed by the recipient facility i which is generated by the CGS during the period p
| Units | - | MWh/p | mass or volume/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | % | GJ/mass or volume | tCO2/GJ | tCO2/p
| Estimated Values | 1 | 9330.2068 |  |  | 0.87 | 0 | 0 |  |  |  |  | 8117.2799
|  | 2 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 3 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 4 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 5 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 6 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 7 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 8 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 9 |  |  |  |  | 0 | 0 |  |  |  |  | 0
|  | 10 |  |  |  |  | 0 | 0 |  |  |  |  | 0
| Total | - | - |  |  | - | - | - | - | - |  | - | 8117.2799
Table 5: Ex-ante estimation of reference emissions for heating energy consumed by the recipient facility which is generated by the CGS
| parameters | Identification No. | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante |  | Ex-ante estimation of reference emissions
|  | i | HCi,p | ηRE | EFfuel,RE | REheat,i,p
| Description of data | Identification number for the recipient facility to which electricity and heat generated by the CGS is supplied | Heating energy consumption by the recipient facility i which is generated by the CGS during the period p | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler (CO2 emission factor of natural gas is applied in this methodology) | Reference emissions for heat consumed by the recipient facility i which is generated by the CGS during the period p
| Units | - | GJ/p | % | tCO2/GJ | tCO2/p
| Estimated Values | 1 |  | 89 | 0 | 0
|  | 2 |  | 89 | 0 | 0
|  | 3 |  | 89 | 0 | 0
|  | 4 |  | 89 | 0 | 0
|  | 5 |  | 89 | 0 | 0
|  | 6 |  | 89 | 0 | 0
|  | 7 |  | 89 | 0 | 0
|  | 8 |  | 89 | 0 | 0
|  | 9 |  | 89 | 0 | 0
|  | 10 |  | 89 | 0 | 0
| Total | - | - | - | - | 0
Table 6: Ex-ante estimation of reference emissions and project emissions by reference chiller
| parameters | Identification No. | Parameters to be monitored ex post |  |  | Parameters to be monitored ex post (in case of EFelec,j is calculated from measured data) |  | Project-specific parameters to be fixed ex ante | [9 empty] | Ex-ante estimation of reference emissions | Ex-ante estimation of project emissions
|  | j | CPJ,j,p | ECPJ,CL,j,p | FCPJ,CL,j,p | FCcap,j,p | EGcap,j,p | COPRE,j | EFelec,j | EFelec,j | EFelec,j | EFelec,j | ηcap,j | NCVfuel,cap,j | EFfuel,cap,j | NCVfuel,CL,j | EFfuel,CL,j | REchiller,j,p | PEchiller,j,p
| Description of data | Identification number of the project absorption chiller | Cooling energy generated by the project absorption chiller j during the period p | Electricity consumption by project absorption chiller j during the period p | Gas fuel consumption by project absorption chiller j during the period p | Amount of fuel consumed by the captive power generation system connected to the absorption chiller j during the period p | Amount of electricity generated by the captive power generation system connected to the absorption chiller j during the period p | COP of reference chiller j | [For grid electricity] CO2 emission factor for consumed electricity by the project absorption chiller j | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option a | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option b | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j | Power generation efficiency of the captive power generation system connected to the project absorption chiller j | Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j | CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j | Net calorific value of gas fuel consumed by the project absorption chiller j | CO2 emission factor for gas fuel consumed by the project absorption chiller j | Reference emissions by reference chiller j during the period p | Project emissions by reference chiller j during the period p
| Units | - | MWh/p | MWh/p | Nm3/p | mass or volume/p | MWh/p | dimensionless | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | % | GJ/mass or volume | tCO2/GJ | GJ/mass or volume | tCO2/GJ | tCO2/p | tCO2/p
| Estimated Values | 1 | 6540.6708 | 0 |  |  |  | 5.69 | 0.89 | 0 | 0 | [6 empty] | 1023.0575 | 0
|  | 2 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 3 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 4 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 5 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 6 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 7 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 8 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 9 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 10 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 11 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 12 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 13 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 14 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 15 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 16 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 17 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 18 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 19 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
|  | 20 | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
| Total | - | - |  |  | - | - | - | - | - | - | - | - | - | - |  |  | 1023.0575 | 0

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 3863.3814 | tCO2/p | ERp
2. Selected default values, etc.
| Reference boiler efficiency |  |  |  | N/A | 89 | % | ηRE
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 9140.3374 | tCO2/p | REp
|  | Reference emissions for electricity consumed by the recipient facility(ies) which is generated by the CGS |  |  | N/A | 8117.2799 | tCO2/p | REelec,i,p
|  | Reference emissions for heat consumed by the recipient facility(ies) which is generated by the CGS |  |  | N/A | 0 | tCO2/p | REheat,i,p
|  | Reference emissions by reference chiller |  |  | N/A | 1023.0575 | tCO2/p | REchiller,j,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 5276.9559 | tCO2/p | PEp
|  | Project emissions from the CGS during the period p |  |  | Gas | 5276.9559 | tCO2/p | PEPJ,CGS,p
|  |  | Gas fuel consumption by the CGS during the period p |  | Gas | 2641968 | mass or volume/p | FCCGS,p
|  |  | Net calorific value of gas fuel consumed by the CGS |  | Gas | 0.03426 | GJ/mass or volume | NCVfuel,CGS
|  |  | CO2 emission factor for gas fuel consumed by the CGS |  | Gas | 0.0583 | tCO2/GJ | EFfuel,PJ
|  | Project emissions from project absorption chiller during the period p |  |  | N/A | 0 | tCO2/p | PEPJ,chiller,p
[List of Default Values]
|  | ηRE |  | Reference boiler efficiency | 89 | %
|  | COPRE,j |  | Cooling capacity per unit (300<=x<=350USRt) | 5.46 | -
|  |  |  | Cooling capacity per unit (350<x<=550USRt) | 5.69 | -
|  |  |  | Cooling capacity per unit (550<x<=750USRt) | 5.9 | -
|  |  |  | Cooling capacity per unit (750<x<=1300USRt) | 6.03 | -

## MSS
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| General Manager PT. DENSO Indonesia | In charge of authorizing the monitoring report.
| Assistant Section Manager PT. DENSO Indonesia | In charge of approving the archived data after being checked and corrected when necessary and preparation of monitoring report.
| Technician PT. DENSO Indonesia | In charge of monitoring procedure (data collection and storage), including monitoring equipments and calibrations, and training of monitoring personnel.
| Junior Technician PT. DENSO Indonesia | In charge of checking the archived data.

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECi,p | Electricity consumption by the recipient facility i which is generated by the CGS during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MRS(input_separate)" sheet
|  | (2) | HCi,p | Heating energy consumption by the recipient facility i which is generated by the CGS during the period p | - | GJ/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of heating energy consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MRS(input_separate)" sheet
|  | (3) | CPJ,j,p | Cooling energy generated by the project absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of cooling energy consumed by the recipient facility i which is generated by the CGS can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MRS(input_separate)" sheet
|  | (4) | FCPJ,CGS,p | Gas fuel consumption by the CGS during the period p |  | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously
|  | (5) | ECPJ,CL,j,p | Electricity consumption by project absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. When project absorption chiller consumes electricity only generated by the project CGS, this parameter can be omitted or equal to zero (0), since CO2 emissions from electricity consumption by project absorption chiller are included in project emissions from the CGS. | Continuously | Input on "MRS(input_separate)" sheet
|  | (6) | FCPJ,CL,j,p | Gas fuel consumption by project absorption chiller j during the period p | - | Nm3/p | Option C | Monitored data | The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MRS(input_separate)" sheet
Table 1-annex: Parameters monitored ex post (in case of EFelec,i and or EFelec,j is calculated from measured data)
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (7) | FCcap,i,p | Amount of fuel consumed by the captive power generation system connected to the recipient facility i during the period p | - | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MRS(input_separate)" sheet
|  | (8) | EGcap,i,p | Amount of electricity generated by the captive power generation system connected to the recipient facility i during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity generated by the captive power generation system connected to the recipient facility i can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MRS(input_separate)" sheet
|  | (9) | FCcap,j,p | Amount of fuel consumed by the captive power generation system connected to the absorption chiller j during the period p | - | mass or volume/p | Option B or Option C | Invoice or Monitored data | [Option B] Data on invoice provided by gas fuel supplier [Option C] The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Monthly or Continuously | Input on "MRS(input_separate)" sheet
|  | (10) | EGcap,j,p | Amount of electricity generated by the captive power generation system connected to the absorption chiller j during the period p | - | MWh/p | Option C | Monitored data | Measuring instrument(s) is installed at the point(s) where the amount of electricity generated by the captive power generation system connected to the absorption chiller j can be measured. The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of validation. | Continuously | Input on "MRS(input_separate)" sheet
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηRE |  | Reference boiler efficiency |  | 89 | % | Value derived from the result of survey. The default value, 89 [%], should be revised if necessary.
| NCVfuel,CGS |  | Net calorific value of gas fuel consumed by the CGS |  | 0.03426 | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFfuel,RE |  | CO2 emission factor for fossil fuel consumed by the reference boiler (CO2 emission factor of natural gas is applied in this methodology) |  | 0 | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel,CGS |  | CO2 emission factor for gas fuel consumed by the CGS |  | 0.0583 | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFelec,i |  | [For grid electricity] CO2 emission factor for consumed electricity in the recipient facility i |  | - | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,i |  | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option a |  | - | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i. |  |  | Calculated
| EFelec,i |  | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option b |  | - | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated; Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i. |  |  | Calculated
| EFelec,i |  | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants. |  |  | Input on "MPS(input_separate)" sheet
| ηcap,i |  | Power generation efficiency of the captive power generation system connected to the recipient facility i |  | - | % | Specification of the captive power generation system connected to the recipient facility i, provided by the manufacturer. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,cap,i |  | Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,cap,i |  | CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| COPRE,j |  | COP of reference chiller j |  | - | dimensionless | Specifications of project chiller j prepared for the quotation or factory acceptance test data by manufacturer. The default COP values are derived from the result of survey on COP of chillers from manufacturers that have high market share. The survey should prove the use of clear methodology. The default COP values should be revised if necessary from survey result which is conducted by JC or project participants. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,j |  | [For grid electricity] CO2 emission factor for consumed electricity by the project absorption chiller j |  | - | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. |  |  | Input on "MPS(input_separate)" sheet
| EFelec,j |  | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option a |  | - | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j. |  |  | Calculated
| EFelec,j |  | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option b |  | - | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated; Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j; and CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j. |  |  | Calculated
| EFelec,j |  | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants. |  |  | Input on "MPS(input_separate)" sheet
| ηcap,j |  | Power generation efficiency of the captive power generation system connected to the project absorption chiller j |  | - | % | Specification of the captive power generation system connected to the project absorption chiller j, provided by the manufacturer. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,cap,j |  | Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,cap,j |  | CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
| NCVfuel,CL,j |  | Net calorific value of gas fuel consumed by the project absorption chiller j |  | - | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied. |  |  | Input on "MPS(input_separate)" sheet
| EFfuel,CL,j |  | CO2 emission factor for gas fuel consumed by the project absorption chiller j |  | - | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | Input on "MPS(input_separate)" sheet
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period | CO2 emission reductions |  | Units
|  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(input_separate)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Report Sheet (Input Separate Sheet) [For Verification]
Table 4: Ex-post calculation of reference emissions for electricity consumed by the recipient facility which is generated by the CGS
| parameters | Identification No. | Parameters monitored ex post | Parameters monitored ex post (in case of EFelec,i is calculated from measured data) |  | Project-specific parameters fixed ex ante | [6 empty] | Ex-post calculation of reference emissions
|  | i | ECi,p | FCcap,i,p | EGcap,i,p | EFelec,i | EFelec,i | EFelec,i | EFelec,i | ηcap,i | NCVfuel,cap,i | EFfuel,cap,i | REelec,i,p
| Description of data | Identification number for the recipient facility to which electricity and heat generated by the CGS is supplied | Electricity consumption by the recipient facility i which is generated by the CGS during the period p | Amount of fuel consumed by the captive power generation system connected to the recipient facility i during the period p | Amount of electricity generated by the captive power generation system connected to the recipient facility i during the period p | [For grid electricity] CO2 emission factor for consumed electricity in the recipient facility i | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option a | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i Option b | [For captive electricity] CO2 emission factor for consumed electricity in the recipient facility i | Power generation efficiency of the captive power generation system connected to the recipient facility i | Net calorific value of the fuel consumed by the captive power generation system connected to the recipient facility i | CO2 emission factor for the fuel consumed by the captive power generation system connected to the recipient facility i | Reference emissions for electricity consumed by the recipient facility i which is generated by the CGS during the period p
| Units | - | MWh/p | mass or volume/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | % | GJ/mass or volume | tCO2/GJ | tCO2/p
| Monitored/ Estimated Values | 1 |  |  |  | 0.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 8 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 9 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | - | - |  |  | - | - | - | - | - |  | - | 0
Table 5: Ex-post calculation of reference emissions for heating energy consumed by the recipient facility which is generated by the CGS
| parameters | Identification No. | Parameters monitored ex post | Project-specific parameters fixed ex ante |  | Ex-post calculation of reference emissions
|  | i | HCi,p | ηRE | EFfuel,RE | REheat,i,p
| Description of data | Identification number for the recipient facility to which electricity and heat generated by the CGS is supplied | Heating energy consumption by the recipient facility i which is generated by the CGS during the period p | Reference boiler efficiency | CO2 emission factor for fossil fuel consumed by the reference boiler (CO2 emission factor of natural gas is applied in this methodology) | Reference emissions for heat consumed by the recipient facility i which is generated by the CGS during the period p
| Units | - | GJ/p | % | tCO2/GJ | tCO2/p
| Monitored/ Estimated Values | 1 |  | 89 | 0 | 0
|  | 2 |  | 89 | 0 | 0
|  | 3 |  | 89 | 0 | 0
|  | 4 |  | 89 | 0 | 0
|  | 5 |  | 89 | 0 | 0
|  | 6 |  | 89 | 0 | 0
|  | 7 |  | 89 | 0 | 0
|  | 8 |  | 89 | 0 | 0
|  | 9 |  | 89 | 0 | 0
|  | 10 |  | 89 | 0 | 0
| Total | - | - | - | - | 0
Table 6: Ex-post calculation of reference emissions and project emissions by reference chiller
| parameters | Identification No. | Parameters monitored ex post |  |  | Parameters monitored ex post (in case of EFelec,j is calculated from measured data) |  | Project-specific parameters fixed ex ante | [9 empty] | Ex-post calculation of reference emissions | Ex-post calculation of project emissions
|  | j | CPJ,j,p | ECPJ,CL,j,p | FCPJ,CL,j,p | FCcap,j,p | EGcap,j,p | COPRE,j | EFelec,j | EFelec,j | EFelec,j | EFelec,j | ηcap,j | NCVfuel,cap,j | EFfuel,cap,j | NCVfuel,CL,j | EFfuel,CL,j | REchiller,j,p | PEchiller,j,p
| Description of data | Identification number of the project absorption chiller | Cooling energy generated by the project absorption chiller j during the period p | Electricity consumption by project absorption chiller j during the period p | Gas fuel consumption by project absorption chiller j during the period p | Amount of fuel consumed by the captive power generation system connected to the absorption chiller j during the period p | Amount of electricity generated by the captive power generation system connected to the absorption chiller j during the period p | COP of reference chiller j | [For grid electricity] CO2 emission factor for consumed electricity by the project absorption chiller j | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option a | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j Option b | [For captive electricity] CO2 emission factor for consumed electricity by the project absorption chiller j | Power generation efficiency of the captive power generation system connected to the project absorption chiller j | Net calorific value of the fuel consumed by the captive power generation system connected to the project absorption chiller j | CO2 emission factor for the fuel consumed by the captive power generation system connected to the project absorption chiller j | Net calorific value of gas fuel consumed by the project absorption chiller j | CO2 emission factor for gas fuel consumed by the project absorption chiller j | Reference emissions by reference chiller j during the period p | Project emissions by reference chiller j during the period p
| Units | - | MWh/p | MWh/p | Nm3/p | mass or volume/p | MWh/p | dimensionless | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | % | GJ/mass or volume | tCO2/GJ | GJ/mass or volume | tCO2/GJ | tCO2/p | tCO2/p
| Monitored/ Estimated Values | 1 | [5 empty] | 5.69 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 6 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 8 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 9 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 12 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 14 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 16 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 17 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 18 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 19 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | - | - |  |  | - | - | - | - | - | - | - | - | - | - |  |  | 0 | 0

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM023_ver01.0
Reference Number: ID028
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| Reference boiler efficiency |  |  |  | N/A | 89 | % | ηRE
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions for electricity consumed by the recipient facility(ies) which is generated by the CGS |  |  | N/A | 0 | tCO2/p | REelec,i,p
|  | Reference emissions for heat consumed by the recipient facility(ies) which is generated by the CGS |  |  | N/A | 0 | tCO2/p | REheat,i,p
|  | Reference emissions by reference chiller |  |  | N/A | 0 | tCO2/p | REchiller,j,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions from the CGS during the period p |  |  | Gas | 0 | tCO2/p | PEPJ,CGS,p
|  |  | Gas fuel consumption by the CGS during the period p |  | Gas | 0 | mass or volume/p | FCCGS,p
|  |  | Net calorific value of gas fuel consumed by the CGS |  | Gas | 0.03426 | GJ/mass or volume | NCVfuel,CGS
|  |  | CO2 emission factor for gas fuel consumed by the CGS |  | Gas | 0.0583 | tCO2/GJ | EFfuel,PJ
|  | Project emissions from project absorption chiller during the period p |  |  | N/A | 0 | tCO2/p | PEPJ,chiller,p
[List of Default Values]
|  | ηRE |  | Reference boiler efficiency | 89 | %
|  | COPRE,j |  | Cooling capacity per unit (300<=x<=350USRt) | 5.46 | -
|  |  |  | Cooling capacity per unit (350<x<=550USRt) | 5.69 | -
|  |  |  | Cooling capacity per unit (550<x<=750USRt) | 5.9 | -
|  |  |  | Cooling capacity per unit (750<x<=1300USRt) | 6.03 | -