## MPS(input)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,p | Total electricity consumption of project DC during the period p | 953.4331 | MWh/p | Option C | monitored data | Measured with an electricity meter(s). Electricity meter readings at the beginning and end of each monitoring period will be documented with photographs showing clearly the meter readings and the date when the meter reading is taken. The meters are installed and managed by the electrical utilities of Lao PDR. | Monitored continuously, recorded at least at the beginning and the end of the monitoring period
| (2) | ƩECIT,i,p | Sum of electricity consumption by IT equipment measured by electricity meters during the period p | 744.8696 | MWh/p | Option C | monitored data | Measured with electricity meters. Electricity meter readings at the beginning and end of each monitoring period will be documented with photographs showing clearly the meter readings and the date when the meter reading is taken. Calibration certificates are issued for all 48 meters by Japan Electric Meters Inspection Corporation (JEMIC), and are valid until November 2023. | Monitored continuously, recorded at least at the beginning and the end of the monitoring period | Input on "MPS(input_separate_IT)" sheet
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor of electricity consumed |  | 0.5595 | tCO2/MWh | [Laotian national grid emission factor] The most recent value announced by the Ministry of Natural Resources and Environment (MONRE), DNA for CDM unless otherwise instructed by the Joint Committee. Source of data: Simplified CM as in "Calculation for the emission factor for electricity generation in Lao PDR, 2010". |  |  | N/A
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 300 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS (input_separate_IT)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
i | ECIT,i,p
An index variable for electricity meters, measuring electricity consumption of IT equipment | Electricity consumption of IT equipment measured by electricity meter i during the period p
- | MWh/p
1 | 15.5181
2 | 15.5181
3 | 15.5181
4 | 15.5181
5 | 15.5181
6 | 15.5181
7 | 15.5181
8 | 15.5181
9 | 15.5181
10 | 15.5181
11 | 15.5181
12 | 15.5181
13 | 15.5181
14 | 15.5181
15 | 15.5181
16 | 15.5181
17 | 15.5181
18 | 15.5181
19 | 15.5181
20 | 15.5181
21 | 15.5181
22 | 15.5181
23 | 15.5181
24 | 15.5181
25 | 15.5181
26 | 15.5181
27 | 15.5181
28 | 15.5181
29 | 15.5181
30 | 15.5181
31 | 15.5181
32 | 15.5181
33 | 15.5181
34 | 15.5181
35 | 15.5181
36 | 15.5181
37 | 15.5181
38 | 15.5181
39 | 15.5181
40 | 15.5181
41 | 15.5181
42 | 15.5181
43 | 15.5181
44 | 15.5181
45 | 15.5181
46 | 15.5181
47 | 15.5181
48 | 15.5181

## MPS(calc_process)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 300.0633 | tCO2/p | ERp
2. Selected default values, etc.
| Energy efficiency (PUE) of reference DC |  |  | N/A | 2 | - | ηREF
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 833.5091 | tCO2/p | REp
|  | Total electricity consumption of project DC during the period p |  | Electricity | 953.4331 | MWh/p | ECPJ,p
|  | Sum of electricity consumption by IT equipment measured by electricity meters during the period p |  | Electricity | 744.8696 | MWh/p | ƩECIT,i,p
|  | CO2 emission factor of electricity consumed |  | Electricity | 0.5595 | tCO2/MWh | EFelec
|  | Energy efficiency (PUE) of reference DC |  | N/A | 2 | - | ηREF
|  | Energy efficiency (PUE) of project DC during the period p |  | N/A | 1.28 | - | ηPJ,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 533.4458 | tCO2/p | PEp
|  | Total electricity consumption of project DC during the period p |  | Electricity | 953.4331 | MWh/p | ECPJ,p
|  | CO2 emission factor of electricity consumed |  | Electricity | 0.5595 | tCO2/MWh | EFelec
[List of Default Values]
|  |  | Energy efficiency (PUE) of reference DC | 2 | -

## MSS
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| JCM Project Manager | Oversees the planning, implementation, and tracking the tasks within the JCM validation and verification procedures Responsible for communication with TPE and the Secretariat
| JCM Monitoring Manager | Archiving the monitoring data Analysis of the monitored data Preparation of the monitoring report Aggregating and archiving the repair/replacement incidence report from JCM Facilities Manager Reporting to JCM Project Manager
| JCM Facilities Manager | Oversees the operation of JCM facilities Reporting of repair/replacement incidence of the project transformers to the JCM Monitoring Manager

## MRS(input)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,p | Total electricity consumption of project DC during the period p |  | MWh/p | Option C | monitored data | Measured with an electricity meter(s). Electricity meter readings at the beginning and end of each monitoring period will be documented with photographs showing clearly the meter readings and the date when the meter reading is taken. In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such electricity meters are required to be calibrated, unless the meters are installed and managed by the electrical utilities of Lao PDR. | Monitored continuously, recorded at least at the beginning and the end of the monitoring period | N/A
|  | (2) | ƩECIT,i,p | Sum of electricity consumption by IT equipment measured by electricity meters during the period p | 0 | MWh/p | Option C | monitored data | Measured with electricity meters. Electricity meter readings at the beginning and end of each monitoring period will be documented with photographs showing clearly the meter readings and the date when the meter reading is taken. In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such electricity meters are required to be calibrated, unless the meters are installed and managed by the electrical utilities of Lao PDR. | Monitored continuously, recorded at least at the beginning and the end of the monitoring period | Input on "MPS(input_separate_IT)" sheet
Table 2: Project-specific parameters fixed ex ante
| (a) | (b) |  |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor of electricity consumed |  |  | 0.5595 | tCO2/MWh | [Laotian national grid emission factor] The most recent value announced by the Ministry of Natural Resources and Environment (MONRE), DNA for CDM unless otherwise instructed by the Joint Committee. Source of data: Simplified CM as in "Calculation for the emission factor for electricity generation in Lao PDR, 2010". |  |  | N/A
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period |  | CO2 emission reductions |  | Units
|  |  | #DIV/0! |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS (input_separate_IT)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
i | ECIT,i,p
An index variable for electricity meters, measuring electricity consumption of IT equipment | Electricity consumption of IT equipment measured by electricity meter i during the period p
- | MWh/p

## MRS(calc_process)
Monitoring Spreadsheet: JCM_LA_AM001_ver01.0
Reference Number: LA001
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | #DIV/0! | tCO2/p | ERp
2. Selected default values, etc.
| Energy efficiency (PUE) of reference DC |  |  | N/A | 2 | - | ηREF
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | #DIV/0! | tCO2/p | REp
|  | Total electricity consumption of project DC during the period p |  | Electricity | 0 | MWh/p | ECPJ,p
|  | Sum of electricity consumption by IT equipment measured by electricity meters during the period p |  | Electricity | 0 | MWh/p | ƩECIT,i,p
|  | CO2 emission factor of electricity consumed |  | Electricity | 0.5595 | tCO2/MWh | EFelec
|  | Energy efficiency (PUE) of reference DC |  | N/A | 2 | - | ηREF
|  | Energy efficiency (PUE) of project DC during the period p |  | N/A | #DIV/0! | - | ηPJ,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Total electricity consumption of project DC during the period p |  | Electricity | 0 | MWh/p | ECPJ,p
|  | CO2 emission factor of electricity consumed |  | Electricity | 0.5595 | tCO2/MWh | EFelec
[List of Default Values]
|  |  | Energy efficiency (PUE) of reference DC | 2 | -