## MPS(input)
Monitoring Spreadsheet: JCM_MN_AM002_ver01.0
Reference Number: MN001
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | PHp | Net heat quantity supplied by the project HOB during the period p. | 4725 | GJ/p | Option C | Logged data of net heat quantity supplied by the project HOB | PHp (Net heat quantity) is measured by the heatmeter. The method of the installation and operational monitoring regarding the heatmeter meets the Mongolian National Standard (MNS). This Standard is "MNS 6241:2011" ("Heatmeters. General requirements for the installation, commissioning, operational monitoring and maintenance"). Accepted uncertainty is ±5% according to "MNS 4549:2005" ("Calculator of heatmeter. The method and means of verification"). Since the heatmeter with the verification (official approval) is used, the heatmeter shall be verified before the verification validity of the heatmeter expire. The verification period of the heatmeter is 4 years according to "List of Measuring Instruments subject to mandatory verification", approved by the order #A384, of 2014/12/09, of the Chairman of the "Mongolian Agency for Standardization and Metrology" under "LAW ON GUARANTEE THE UNIFORMITY OF MEASUREMENT". QA/QC: The installed heatmeter shall be confirmed by Verification Validity with Verification Seal marked on the heatmeter. In case that the heatmeter does not meet MNS, the heatmeter shall be replaced by a new one with the verification. Monitoring data is the amount of heat supplied from the project HOB. This monitoring data is recorded in the data logger that is built into the heatmeter. Electric data recorded on the data logger is input to the spreadsheet properly. The measuring frequency is continuous. The monitoring data is recorded hourly and collected daily. The backup method is the daily back-up in the computer and monthly back-up on the CD. QA/QC: Monitored data are managed according to the QA/QC procedures stipulated in the Monitoring Structure Sheet. | Measuring frequency: Continuously Recording frequency: Hourly | Trouble shooting procedure of missing data; Completed by the hourly minimum value (excluding abnormal value) of available recorded data during the monitoring period.
| 2 | HMPp | Total hours of the project HOB operation during the period p | 5088 | hours/p | Option C | Identified by monitoring period | Total time from the start time of monitoring to the end time of monitoring | --- | ---
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| RPCPJ,HOB | Rated power consumption of the project HOB |  | 1.2 | kW | Catalog value provided by the manufacturer of the project HOB
| EFCO2,grid | CO2 emission factor of the grid electricity consumed by the project HOB |  | 1.103 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from CDM Mongolia unless otherwise instructed by the Joint Committee.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 92 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)
Monitoring Spreadsheet: JCM_MN_AM002_ver01.0
Reference Number: MN001
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 92 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor of coal |  |  |  | Coal | 0.0909 | tCO2/GJ | EFCO2, coal
| Boiler efficiency of the reference HOB |  |  |  | N/A | 0.533 | - | ηRE,HOB
| Boiler efficiency of the project HOB |  |  |  | N/A | 0.61 | - | ηPJ,HOB
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 805 | tCO2/p | REp
|  | Reference Emissions |  |  | N/A | 805 | tCO2/p
|  |  | Net heat quantity supplied by the project HOB |  | N/A | 4725 | GJ/p | PHp
|  |  | Boiler efficiency of the reference HOB |  | N/A | 0.533 | - | ηRE,HOB
|  |  | CO2 emission factor of coal |  | Coal | 0.0909 | tCO2/GJ | EFCO2,coal
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 713 | tCO2/p | PEp
|  | Project emissions (Fossil fuel consumption) |  |  | N/A | 705 | tCO2/p
|  |  | Net heat quantity supplied by the project HOB |  | N/A | 4725 | GJ/p | PHp
|  |  | Boiler efficiency of the project HOB |  | N/A | 0.61 | - | ηPJ,HOB
|  |  | CO2 emission factor of coal |  | Coal | 0.0909 | tCO2/GJ | EFCO2,coal
|  | Project emissions (Electricity consumption) |  |  | N/A | 8 | tCO2/p
|  |  | Electricity consumption of the project HOB |  | Electricity | 7 | MWh/p | ECp
|  |  | Total hours of the project HOB operation |  | N/A | 5088 | h/p | HMPp
|  |  | Rated power consumption of the project HOB |  | N/A | 1.2 | kW | RPCPJ,HOB
|  |  | CO2 emission factor of the grid |  | Electricity | 1.103 | tCO2/MWh | EFCO2,grid
[List of Default Values]
|  |  |  | CO2 Emission Factor of Coal used in HOBs | EFCO2, coal | unit
|  |  |  | Default emission factor applied to Lignite in fuel according to “2006 IPCC Guidelines for National Greenhouse Gas Inventory” | 0.0909 | tCO2/GJ
|  |  |  | Boiler Efficiency of coal-fired HOB in Mongolia | η | unit
|  |  |  | Boiler Efficiency of Reference the HOB | 0.533 | -
|  |  |  | Boiler Efficiency of the Project HOB | 0.61 | -

## MSS
Monitoring Spreadsheet: JCM_MN_AM002_ver01.0
Reference Number: MN001
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Senior Engineer of Anu-Service Co.,Ltd | Operation of HOB; Management of HOB; Maintenance of HOB.
| Job Manager of SUURI-KEIKAKU CO.LTD. | Administrative Agent of JCM Project; making and submitting PDD; management of QA/QC of monitoring data; responsible for overall monitoring activity; ensures the quality of the monitoring report and the structure and procedure for producing such a document; appoints the civil engineer of ANU-SERVICE CO.,LTD. responsible for managing monitoring points, when necessary, to collect data and maintain and control measuring insrruments (including calibration/regular inspection) at monitoring points.
| Civil Engineer of ANU-SERVICE CO.,LTD. | Archiving the monitoring data; responsible for managing monitoring points, when necessary, to collect data and maintain and control measuring instruments (including calibration/regular inspection) at monitoring points; Operation of Telemeter System of Heatmeter; Management of Telemeter System of Heatmeter; Development of Telemeter System of Heatmeter; Maintenance of Telemeter System of Heatmeter.

## MRS(input)
Monitoring Spreadsheet: JCM_MN_AM002_ver01.0
Reference Number: MN001
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | 1 | PHp | Net heat quantity supplied by the project HOB during the period p. |  | GJ/p | Option C | Logged data of net heat quantity supplied by the project HOB | Measurement methods which are using a heatmeter meet the industrial standards (host country or international standard). Monitoring data is the amount of heat supplied from the project HOB. This monitoring data is recorded in the data logger that is built into the heat meter. Electric data recorded on the data logger is input to the spreadsheet properly. In these monitoring activities, QA/QC be implemented. - In the case that heatmeter with verification is used, the verification validity for the heatmeter does not expire till the last date of the monitoring period. - If the heatmeter with the verification is not required in the industrial standard, uncertainty of the calibration data of the monitoring equipment meet the following conditions; - It is within accepted level of the verification. - It is within the accuracy level of industry standard requires. Required calibration frequency is the frequency which can be confirmed to be within the accuracy level of the requirement of industrial standard. | Measuring frequency: Continuously Recording frequency: Hourly | Trouble shooting procedure of missing data; Completed by the hourly minimum value (excluding abnormal value) of available recorded data during the monitoring period.
|  | 2 | HMPp | Total hours of the project HOB operation during the period p |  | hours/p | Option C | Identified by monitoring period | Total time from the start time of monitoring to the end time of monitoring | --- | ---
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| RPCPJ,HOB |  | Rated power consumption of the project HOB |  | 1.2 | kW | Catalog value provided by the manufacturer of the project HOB
| EFCO2,grid |  | CO2 emission factor of the grid electricity consumed by the project HOB |  | 1.103 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from CDM Mongolia unless otherwise instructed by the Joint Committee.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_MN_AM002_ver01.0
Reference Number: MN001
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor of coal |  |  |  | Coal | 0.0909 | tCO2/GJ | EFCO2, coal
| Boiler efficiency of the reference HOB |  |  |  | N/A | 0.533 | - | ηRE,HOB
| Boiler efficiency of the project HOB |  |  |  | N/A | 0.61 | - | ηPJ,HOB
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 0 | tCO2/p | REp
|  | Reference Emissions |  |  | N/A | 0 | tCO2/p
|  |  | Net heat quantity supplied by the project HOB |  | N/A | 0 | GJ/p | PHp
|  |  | Boiler efficiency of the reference HOB |  | N/A | 0.533 | - | ηRE,HOB
|  |  | CO2 emission factor of coal |  | Coal | 0.0909 | tCO2/GJ | EFCO2,coal
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions (Fossil fuel consumption) |  |  | N/A | 0 | tCO2/p
|  |  | Net heat quantity supplied by the project HOB |  | N/A | 0 | GJ/p | PHp
|  |  | Boiler efficiency of the project HOB |  | N/A | 0.61 | - | ηPJ,HOB
|  |  | CO2 emission factor of coal |  | Coal | 0.0909 | tCO2/GJ | EFCO2,coal
|  | Project emissions (Electricity consumption) |  |  | N/A | 0 | tCO2/p
|  |  | Electricity consumption of the project HOB |  | Electricity | 0 | MWh/p | ECp
|  |  | Total hours of the project HOB operation |  | N/A | 0 | h/p | HMPp
|  |  | Rated power consumption of the project HOB |  | N/A | 1.2 | kW | RPCPJ,HOB
|  |  | CO2 emission factor of the grid |  | Electricity | 1.103 | tCO2/MWh | EFCO2,grid
[List of Default Values]
|  |  |  | CO2 Emission Factor of Coal used in HOBs | EFCO2, coal | unit
|  |  |  | Default emission factor applied to Lignite in fuel according to “2006 IPCC Guidelines for National Greenhouse Gas Inventory” | 0.0909 | tCO2/GJ
|  |  |  | Boiler Efficiency of coal-fired HOB in Mongolia | η | unit
|  |  |  | Boiler Efficiency of Reference the HOB | 0.533 | -
|  |  |  | Boiler Efficiency of the Project HOB | 0.61 | -