## PMS(input)
JCM_MN_F_PMS_ver01.0
Joint Crediting Mechanism Proposed Methodology Spreadsheet Form (input sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | EL,send,y | Power sent from the point of origin/supply to the transmission line L in year y |  | MWh/y | Option C | Electrical power meter | - Type of electrical power meter：Three-phase four-wire system electrical power meter - Specification： Electrical power meter shall be applied for measurement of electrical power loss. Measurement items of the electrical power meter shall be as follows 1) electric energy 2) electric current 3) voltage 4) power factor - Measuring method： 1) An electrical power meter is connected to the secondary side of an instrument transformer. Method for connection of the electrical power meter shall be determined carefully. 2) The electrical power meters shall be connected both of power transmission end and power reception end. Recording mediums shall be provided to record the amount of electric power. 3) Time synchronization of power transmission end and power reception end shall be considered to record the amount of electric power. 4) The transmitted electric power and electric power loss shall be analyzed. - Calibration： 1) During the installation of equipment Certified precise electric power measurement equipment shall be provided. When the electric power measured by the electrical power meter is same result measured by the certified precise electric power measurement equipment, the electrical power meter will be installed 2) Every year after the installation Same method which applied before installation of the electrical power meter will be applied every year after the installation. | Continuous
| 2 | EL,receive,y | Power received at the point of receipt of the transmission line L in year y |  | MWh/y | Option C | Electrical power meter | - Type of electrical power meter：Three-phase four-wire system electrical power meter - Specification： Electrical power meter shall be applied for measurement of electrical power loss. Measurement items of the electrical power meter shall be as follows 1) electric energy 2) electric current 3) voltage 4) power factor - Measuring method： 1) An electrical power meter is connected to the secondary side of an instrument transformer. Method for connection of the electrical power meter shall be determined carefully. 2) The electrical power meters shall be connected both of power transmission end and power reception end. Recording mediums shall be provided to record the amount of electric power. 3) Time synchronization of power transmission end and power reception end shall be considered to record the amount of electric power. 4) The transmitted electric power and electric power loss shall be analyzed. - Calibration： 1) During the installation of equipment Certified precise electric power measurement equipment shall be provided. When the electric power measured by the electrical power meter is same result measured by the certified precise electric power measurement equipment, the electrical power meter will be installed 2) Every year after the installation Same method which applied before installation of the electrical power meter will be applied every year after the installation. | Continuous
| 3 | EFGrid,y | CO2 emission factor of the grid in year y |  | tCO2/MWh | Option A | Value as published by the government | Emission factor for the corresponding year shall be used. If such data is not available, the most recent data available at the time of submission of the monitoring report shall be used. | Annually
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| RdcRF,L | Direct current resistance of transmission line L using currently used transmission conductors |  |  | Ω/km | As per the methodology
| RdcPJ,L | Direct current resistance of transmission line L using LL-ACSR/SA conductors (@20 deg. C) |  |  | Ω/km | Measured according to IEC 60468 (Method of measurement of resistivity of metallic materials).
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| #DIV/0! |  | tCO2/y
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## PMS(calc_process)
JCM_MN_F_PMS_ver01.0
Joint Crediting Mechanism Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period of year y |  |  |  |  | #DIV/0! | tCO2/y | ERy
2. Selected default values, etc.
| Direct current resistance of transmission line L using currently used transmission conductors (@20 deg. C) |  |  |  |  | 0 | Ω/km | RdcRF,L
| Direct current resistance of transmission line L using LL-ACSR/SA conductors (@20 deg. C) |  |  |  |  | 0 | Ω/km | RdcPJ,L
| CO2 emission factor of the grid in year y |  |  |  |  | 0 | tCO2/MWh | EFGrid,y
3. Calculations for reference emissions
| Reference emissions during the period of year y |  |  |  |  | #DIV/0! | tCO2/y | REy
|  | Reference transmission loss at transmission line L in year y |  |  |  | #DIV/0! | MWh/y | LOSSRF,L,y
4. Calculations of the project emissions
| Project emissions during the period of year y |  |  |  |  | 0 | tCO2/y | PEy
|  | Project transmission loss at transmission line L in year y |  |  |  | 0 | MWh/y | LOSSPJ,L,y
|  |  | Power sent from the point of origin/supply to the transmission line L in year y |  |  | 0 | MWh/y | EL,send,y
|  |  | Power received at the point of receipt of the transmission line L in year y |  |  | 0 | MWh/y | EL,receive,y
[List of Default Values]
Direct current resistance of transmission line L using currently used transmission conductors (@20 deg. C)
|  |  |  | LL-ACSR/SA 279/20mm2 | 0.1158 | Ω/km
|  |  |  | LL-ACSR/SA 337/27mm2 | 0.0939 | Ω/km
|  |  |  | LL-ACSR/SA 445/36mm2 | 0.0718 | Ω/km