## AM3_MPS(input)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is calibrated by the manufacturer at the time of factory shipment, and the performance of meter is guaranteed by the manufacturer for ten years without a calibration. - Measuring and recording: The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. | Continuously | Input on "MPS (input_separate)"
| (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p | - | mass or weight/p | - | - | Data is collected and recorded from the invoices by the fuel supply company. | - | -
| (3) | EGPJ,p | The amount of electricity generated during the monitoring period p | - | MWh/p | - | - | Data is measured by measuring equipment in the factory. - Specification of measuring equipment: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | - | -
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated |  |  | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec | Power generation efficiency |  | - | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel | Net calorific value of consumed fuel |  | - | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel | CO2 emission factor of consumed fuel |  | - | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 314 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM3_MPS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
|  | Parameters to be monitored ex post |  |  | Project-specific parameters to be fixed ex ante | [11 empty] | Ex-ante estimation of emissions
Parameters | Chiller i | ECPJ,i,p | FCPJ,p | EGPJ,p | EFelec | EFelec | EFelec | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | ηelec | NCVfuel | EFfuel | REi,p | PEi,p | ERi,p
Description of data | Project chiller No. | Power consumption of project chiller i during the period p | The amount of fuel input for power generation during monitoring period p | The amount of electricity generated during the monitoring period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Power generation efficiency | Net calorific value of consumed fuel | CO2 emission factor of consumed fuel | Reference emissions of project chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | mass or weight/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | % | GJ/mass or weight | tCO2/GJ | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1(U-R-4/1&2) | 2288 | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 1400.6903 | 1295.9232 | 104.7671
| 2(U-R-5/1&2) | 2288 | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 1400.6903 | 1295.9232 | 104.7671
| 3(U-R-6/1&2) | 2288 | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 1400.6903 | 1295.9232 | 104.7671
| 4 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 5 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 6 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 7 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 8 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 9 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 10 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 11 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 12 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 13 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 14 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 15 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 16 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 17 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 18 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 19 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| 20 |  | - | - | 0.5664 | 0 | 0 | - |  |  |  |  | 0 | - | - | - | 0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4202.0708 | 3887.7696 | 314.3012

## AM3_MPS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 314.3012 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 4202.0708 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 4202.0708 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 3887.7696 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 3887.7696 | tCO2/p | PEp
[List of Default Values]
COPRE,i for inverter type
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## AM3_MSS
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| General Manager (stationed in Japan) | Responsible for project management.
| Person-in-charge of the Project (stationed in Japan) | Responsible for facilities, including reporting preparations, equipment adjustments, monitoring and making monitoring report
| General Manager (stationed in Thailand) | Responsible for equipment management and MRV surveys.
| Person-in-charge of the Project (stationed in Thailand) | Responsible for data collecting.

## AM3_MRS(input)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is calibrated by the manufacturer at the time of factory shipment, and the performance of meter is guaranteed by the manufacturer for ten years without a calibration. - Measuring and recording: The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. | Continuously | Input on "MRS (input_separate)"
|  | (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p | - | mass or weight/p | - | - | Data is collected and recorded from the invoices by the fuel supply company. | - | -
|  | (3) | EGPJ,p | The amount of electricity generated during the monitoring period p | - | MWh/p | - | - | Data is measured by measuring equipment in the factory. - Specification of measuring equipment: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | - | -
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated |  |  | Calculated
| EFelec |  | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i |  | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i |  | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i |  | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i |  | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i |  | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec |  | Power generation efficiency |  | - | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel |  | Net calorific value of consumed fuel |  | - | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel |  | CO2 emission factor of consumed fuel |  | - | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM3_MRS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
|  | Parameters monitored ex post |  |  | Project-specific parameters fixed ex ante | [11 empty] | Ex-post calculation of emissions
Parameters | Chiller i | ECPJ,i,p | FCPJ,p | EGPJ,p | EFelec | EFelec | EFelec | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | ηelec | NCVfuel | EFfuel | REi,p | PEi,p | ERi,p
Description of data | Project chiller No. | Power consumption of project chiller i during the period p | The amount of fuel input for power generation during monitoring period p | The amount of electricity generated during the monitoring period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Power generation efficiency | Net calorific value of consumed fuel | CO2 emission factor of consumed fuel | Reference emissions of project chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | mass or weight/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | % | GJ/mass or weight | tCO2/GJ | tCO2/p | tCO2/p | tCO2/p
Monitored /estimated values | 1 |  | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 0 | 0 | 0
| 2 |  | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 0 | 0 | 0
| 3 |  | - | - | 0.5664 | 0 | 0 | - | 37 | 7 | 5.69 | 6.15 | 6.15 | - | - | - | 0 | 0 | 0
| 4 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 5 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 6 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 7 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 8 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 9 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 10 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 11 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 12 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 13 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 14 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 15 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 16 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 17 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 18 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 19 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| 20 |  | - | - | 0.5664 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | - | - | - | 0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | 0 | 0

## AM3_MRS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number: TH003
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
COPRE,i for inverter type
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## AM6_MPS(input)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,DV,i,j,k,p | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | - | MWh/p | Option C | Monitored data | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is calibrated by the manufacturer at the time of factory shipment, and the performance of meter is guaranteed by the manufacturer for ten years without a calibration. - Measuring and recording: The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. | Continuously | Input on "MPS (input_separate)"
| (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p | - | mass or weight/p | - | - | Data is collected and recorded from the invoices by the fuel supply company. | - | -
| (3) | EGPJ,p | The amount of electricity generated during the monitoring period p | - | MWh/p | - | - | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is replaced or calibrated at an interval following the regulations in the country in which the electricity meter is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the electrical power meter has been prepared by the time of installation. | - | -
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec,k | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated. |  |  | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| AFRRE,j,k | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document of the cleanroom. |  |  | Calculated
| AFRPJ,j,k | Airflow rate of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "MPS (input_separate)"
| Pd,RE,j,k | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | 1200 | Pa | Hearing survey with manufacturer of mixing ventilation air conditioning unit. |  |  | Default value
| Pd,PJ,j,k | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | Pa | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "MPS (input_separate)"
| Vcr,j,k | Volume of the cleanroom j in the project factory k |  | - | m3 | Design document of the cleanroom. |  |  | Input on "MPS (input_separate)"
| Tvent,j,k | Number of times of ventilation required for the cleanroom j in the project factory k |  | - | times/h | Multiple documents published on the web. The default value is determined from the table corresponding to the airborne particulate cleanliness class required for the cleanroom. |  |  | Input on "MPS (input_separate)" Select from default values
| ηelec | Power generation efficiency |  | - | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel | Net calorific value of consumed fuel |  | - | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel | CO2 emission factor of consumed fuel |  | - | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 3430 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM6_MPS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Table 4: Ex-ante estimation of reference emissions
|  | Identification numbers |  |  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [9 empty] | Ex-ante estimation of reference emissions
| Parameters | i | j | k | ECPJ,DV,i,j,k,p | EFelec | EFelec | EFelec | EFelec | AFRRE,j,k | AFRPJ,i,j,k | Pd,RE,j,k | Pd,PJ,j,k | Vcr,j,k | Tvent,j,k | REi,p
| Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Airflow rate of project displacement ventilation air conditioning unit i supplying air to cleanroom j in the project factory k | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Volume of the cleanroom j in the project factory k | Number of times of ventilation required for the cleanroom j in the project factory k | Reference emissions of the reference mixing ventilation air conditioning unit i during the period p
| Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | m3/s | m3/s | Pa | Pa | m3 | times/h | tCO2/p
| Estimated values | A-4P11 BR2 10k(12unit) | BR2 10k | building2 | 115.2 | 0.5664 | 0 | 0 | - | 42.7111 | 24.5 | 1200 | 208 | 3844 | 40 | 656.2486 | 0
|  | A-4P12 BR3 1K(34unit) | BR3 1K | building3 | 326.4 | 0.5664 | 0 | 0 | - | 158.4444 | 69.4167 | 1200 | 247 | 7130 | 80 | 2050.0807 | 80
|  | A-4P13 BR3 10k(35unit) | BR3 10k | building3 | 336 | 0.5664 | 0 | 0 | - | 75.7778 | 71.4583 | 1200 | 208 | 6820 | 40 | 1164.3121 | 40
|  | 4 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 5 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 6 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 7 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 8 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 9 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 10 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 11 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 12 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 13 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 14 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 15 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 16 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 17 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 18 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 19 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | 20 |  |  |  | 0.5664 | 0 | 0 | - | 0 |  | 1200 |  |  |  | 0
|  | Total | - | - | - | - | - | - | - | - | - | - | - | - | - | 3870.6414
Table 5: Ex-ante estimation of project emissions
|  | Identification numbers |  |  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante |  |  |  | Ex-ante estimation of project emissions
| Parameters | i | j | k | ECPJ,DV,i,j,k,p | EFelec | EFelec | EFelec | EFelec | PEi,p
| Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity Option c | Project emissions of the project displacement ventilation air conditioning unit i during the period p
| Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/p
| Estimated values | 1 |  |  | 115.2 | 0.5664 | 0 | 0 | - | 65.2493
|  | 2 |  |  | 326.4 | 0.5664 | 0 | 0 | - | 184.873
|  | 3 |  |  | 336 | 0.5664 | 0 | 0 | - | 190.3104
|  | 4 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 5 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 6 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 7 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 8 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 9 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 10 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 11 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 12 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 13 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 14 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 15 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 16 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 17 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 18 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 19 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 20 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | Total |  |  | - | - | - | - | - | 440.4326

## AM6_MPS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 3430.2088 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 3870.6414 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 3870.6414 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 440.4326 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 440.4326 | tCO2/p | PEp
[List of Default Values]
|  |  | Number of times of ventilation required for the cleanroom | ISO 14644-1:2015 | FED-STD-209E | Tvent,j,k
|  |  |  | Class 6 | 1000 | 80
|  |  |  | Class 7 | 10000 | 40
|  |  | Discharge pressure of reference mixing ventilation air conditioning unit |  | 1200 | Pa

## AM6_MSS
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| General Manager (stationed in Japan) | Responsible for project management.
| Person-in-charge of the Project (stationed in Japan) | Responsible for facilities, including reporting preparations, equipment adjustments, monitoring and making monitoring report
| General Manager (stationed in Thailand) | Responsible for equipment management and MRV surveys.
| Person-in-charge of the Project (stationed in Thailand) | Responsible for data collecting.

## AM6_MRS(input)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,DV,i,j,k,p | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | - | MWh/p | Option C | Monitored data | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is calibrated by the manufacturer at the time of factory shipment, and the performance of meter is guaranteed by the manufacturer for ten years without a calibration. - Measuring and recording: The data monitored and required for verification and issuance will be kept and archived electronically for two years after the final issuance of credits. | Continuously | Input on "MRS (input_separate)"
|  | (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p | - | mass or weight/p | - | - | Data is collected and recorded from the invoices by the fuel supply company. | - | -
|  | (3) | EGPJ,p | The amount of electricity generated during the monitoring period p | - | MWh/p | - | - | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is replaced or calibrated at an interval following the regulations in the country in which the electricity meter is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the electrical power meter has been prepared by the time of installation. | - | -
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec,k |  | [For grid electricity] CO2 emission factor for consumed electricity |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated. |  |  | Calculated
| EFelec |  | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | - | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| AFRRE,j,k |  | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document of the cleanroom. |  |  | Calculated
| AFRPJ,j,k |  | Airflow rate of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "MPS (input_separate)"
| Pd,RE,j,k |  | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | 1200 | Pa | Hearing survey with manufacturer of mixing ventilation air conditioning unit. |  |  | Default value
| Pd,PJ,j,k |  | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | Pa | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "MPS (input_separate)"
| Vcr,j,k |  | Volume of the cleanroom j in the project factory k |  | - | m3 | Design document of the cleanroom. |  |  | Input on "MPS (input_separate)"
| Tvent,j,k |  | Number of times of ventilation required for the cleanroom j in the project factory k |  | - | times/h | Multiple documents published on the web. The default value is determined from the table corresponding to the airborne particulate cleanliness class required for the cleanroom. |  |  | Input on "MPS (input_separate)" Select from default values
| ηelec |  | Power generation efficiency |  | - | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel |  | Net calorific value of consumed fuel |  | - | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel |  | CO2 emission factor of consumed fuel |  | - | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM6_MRS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Table 4: Ex-post calculation of reference emissions
|  | Identification numbers |  |  | Parameters monitored ex post | Project-specific parameters fixed ex ante | [9 empty] | Ex-post calculation of reference emissions
| Parameters | i | j | k | ECPJ,DV,i,j,k,p | EFelec | EFelec | EFelec | EFelec | AFRRE,j,k | AFRPJ,i,j,k | Pd,RE,j,k | Pd,PJ,j,k | Vcr,j,k | Tvent,j,k | REi,p
| Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Airflow rate of project displacement ventilation air conditioning unit i supplying air to cleanroom j in the project factory k | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Volume of the cleanroom j in the project factory k | Number of times of ventilation required for the cleanroom j in the project factory k | Reference emissions of the reference mixing ventilation air conditioning unit i during the period p
| Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | m3/s | m3/s | Pa | Pa | m3 | times/h | tCO2/p
| Monitored /estimated values | 1 |  |  |  | 0.5664 | 0 | 0 | - | 42.7111 | 24.5 | 1200 | 208 | 3844 | 40 | 0 | 0
|  | 2 |  |  |  | 0.5664 | 0 | 0 | - | 158.4444 | 69.4167 | 1200 | 247 | 7130 | 80 | 0 | 80
|  | 3 |  |  |  | 0.5664 | 0 | 0 | - | 75.7778 | 71.4583 | 1200 | 208 | 6820 | 40 | 0 | 40
|  | 4 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 5 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 6 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 7 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 8 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 9 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 10 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 11 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 12 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 13 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 14 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 15 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 16 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 17 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 18 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 19 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | 20 |  |  |  | 0.5664 | 0 | 0 | - | 0 | 0 | 1200 | 0 | 0 | 0 | 0
|  | Total | - | - | - | - | - | - | - | - | - | - | - | - | - | 0
Table 5: Ex-post calculation of project emissions
|  | Identification numbers |  |  | Parameters monitored ex post | Project-specific parameters fixed ex ante |  |  |  | Ex-post calculation of project emissions
| Parameters | i | j | k | ECPJ,DV,i,j,k,p | EFelec | EFelec | EFelec | EFelec | PEi,p
| Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity Option c | Project emissions of the project displacement ventilation air conditioning unit i during the period p
| Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/p
| Monitored /estimated values | 1 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 2 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 3 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 4 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 5 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 6 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 7 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 8 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 9 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 10 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 11 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 12 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 13 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 14 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 15 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 16 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 17 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 18 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 19 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | 20 |  |  | 0 | 0.5664 | 0 | 0 | - | 0
|  | Total |  |  | - | - | - | - | - | 0

## AM6_MRS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM006_ver01.0
Reference Number: TH003
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | Number of times of ventilation required for the cleanroom | ISO 14644-1:2015 | FED-STD-209E | Tvent,j,k
|  |  |  | Class 6 | 1000 | 80
|  |  |  | Class 7 | 10000 | 40
|  |  | Discharge pressure of reference mixing ventilation air conditioning unit |  | 1200 | Pa