## MPS(input)
Monitoring Spreadsheet: JCM_TH_AM017_ver01.0
Reference Number: TH024
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | N | Number of transmission lines in the project area X | 184 | - | Option C | Monitored data | The value is counted in the OPENVQ system. | Continuously
| (2) | Pk,i,t | Active power at the bus k of transmission line i at the time t | - | W | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at every five minutes are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
| (3) | Vk,i,t | Voltage measured at the bus k of transmission line i at the time t | - | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at every five minutes are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
| (4) | Vl,i,t | Voltage measured at the bus l of transmission line i at the time t | - | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at every five minutes are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
| (5) | Qk,i,t | Reactive power at the bus k of transmission line i at the time t | - | var | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at every five minutes are considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
| - | PLRE,X,lines,p | Reference transmission line loss at transmission lines in the project area X during the period p | 530442.3 | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | PLPJ,X,lines,p | Project transmission line loss at transmission lines in the project area X during the period p | 492377.7 | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | PLRE,linei,p | Reference transmission line loss at transmission line i during the period p | - | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | PLRE,linei,t | Reference transmission line loss at transmission line i at the time t | - | W | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | QRE,k,i,t | Reference reactive power at the bus k of transmission line i at the time t | - | var | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | VRE,l,i,t | Reference voltage at the bus l of transmission line i at the time t | - | V | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | PLPJ,linei,p | Project transmission line loss at transmission line i during the period p | - | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| - | PLPJ,linei,t | Project transmission line loss at transmission line i at the time t | - | W | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFGrid | CO2 emission factor for grid |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization, unless otherwise instructed by the Joint Committee.
| Ratiomode | Mode value of Ratiok of Vk,i to the base voltage Vbase,i of transmission line i |  | 1.03 | - | Calculated based on the procedure described in F.2. of the methodology.
| Ri | Resistance of transmission line i |  |  | Ω | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| Xi | Reactance of transmission line i |  |  | Ω | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| Bi | Susceptance of transmission line i |  |  | S | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| T | Measurement interval |  | 5 | min | Predetermined measurement interval
| Vbase,i | Base voltage of transmission line i |  |  | V | Specification of transmission line i |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| VRE,k,i | Reference voltage at the bus k of transmission line i |  | 0 | V | Calculated based on the procedure described in F.2. of the methodology. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 21559 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## Value Vbase,i,Ri,Xi,Bi,VRE,k,i
ID Transmission Line i | R(pu) | X | B | Vbase,I (kV) | Vbase,I (V) | Ri(Ω) | Xi(Ω) | Bi(S) | VRE,k,I (V)
1 | 0.044936 | 0.15415 | 0.02038 | 115 | 115000 | 5.9428 | 20.3866 | 0.0001541 | 118450
2 | 0.044987 | 0.15403 | 0.020381 | 115 | 115000 | 5.9495 | 20.3702 | 0.00015411 | 118450
3 | 0.097413 | 0.28244 | 0.037812 | 115 | 115000 | 12.8829 | 37.3532 | 0.00028591 | 118450
4 | 0.097504 | 0.28222 | 0.037815 | 115 | 115000 | 12.8949 | 37.3239 | 0.00028594 | 118450
5 | 0.029952 | 0.085433 | 0.01114 | 115 | 115000 | 3.9612 | 11.2985 | 8.4234e-05 | 118450
6 | 0.14147 | 0.1718 | 0.019325 | 115 | 115000 | 18.7101 | 22.7199 | 0.00014612 | 118450
7 | 0.00069 | 0.00511 | 0.01044 | 230 | 230000 | 0.36501 | 2.7032 | 1.9735e-05 | 236900
8 | 0.00069 | 0.00511 | 0.01044 | 230 | 230000 | 0.36501 | 2.7032 | 1.9735e-05 | 236900
9 | 0.003634 | 0.010293 | 0.0054 | 115 | 115000 | 0.4806 | 1.3612 | 4.0832e-05 | 118450
10 | 0.044984 | 0.20892 | 0.029495 | 115 | 115000 | 5.9491 | 27.6294 | 0.00022302 | 118450
11 | 0.007268 | 0.020585 | 0.0027 | 115 | 115000 | 0.96119 | 2.7224 | 2.0416e-05 | 118450
12 | 0.024352 | 0.11323 | 0.063896 | 115 | 115000 | 3.2206 | 14.9744 | 0.00048315 | 118450
13 | 0.07505 | 0.21844 | 0.0289 | 115 | 115000 | 9.9254 | 28.8887 | 0.00021853 | 118450
14 | 0.00145 | 0.01582 | 0.06193 | 230 | 230000 | 0.76705 | 8.3688 | 0.00011707 | 236900
15 | 0.00146 | 0.01581 | 0.062 | 230 | 230000 | 0.77234 | 8.3635 | 0.0001172 | 236900
16 | 0.00121 | 0.00746 | 0.00213 | 115 | 115000 | 0.16002 | 0.98658 | 1.6106e-05 | 118450
17 | 0.00121 | 0.00746 | 0.00213 | 115 | 115000 | 0.16002 | 0.98658 | 1.6106e-05 | 118450
18 | 0.09742 | 0.27774 | 0.03629 | 115 | 115000 | 12.8838 | 36.7311 | 0.0002744 | 118450
19 | 0.083195 | 0.24168 | 0.03237 | 115 | 115000 | 11.0025 | 31.9619 | 0.00024476 | 118450
20 | 0.083254 | 0.24161 | 0.03237 | 115 | 115000 | 11.0103 | 31.9533 | 0.00024476 | 118450
21 | 0.062452 | 0.07492 | 0.00842 | 115 | 115000 | 8.2593 | 9.9082 | 6.3667e-05 | 118450
22 | 0.07505 | 0.21844 | 0.0289 | 115 | 115000 | 9.9254 | 28.8887 | 0.00021853 | 118450
23 | 0.027963 | 0.12996 | 0.018407 | 115 | 115000 | 3.6981 | 17.1875 | 0.00013918 | 118450
24 | 0.02603 | 0.11754 | 0.01641 | 115 | 115000 | 3.4425 | 15.5445 | 0.00012408 | 118450
25 | 0.076726 | 0.34641 | 0.04837 | 115 | 115000 | 10.147 | 45.8133 | 0.00036575 | 118450
26 | 0.027963 | 0.12996 | 0.018407 | 115 | 115000 | 3.6981 | 17.1875 | 0.00013918 | 118450
27 | 0.05697 | 0.2616 | 0.03765 | 115 | 115000 | 7.5343 | 34.5966 | 0.00028469 | 118450
28 | 0.011886 | 0.079851 | 0.02142 | 115 | 115000 | 1.5719 | 10.5603 | 0.00016197 | 118450
29 | 0.02505 | 0.11341 | 0.01674 | 115 | 115000 | 3.3129 | 14.9985 | 0.00012658 | 118450
30 | 0.03831 | 0.10922 | 0.01427 | 115 | 115000 | 5.0665 | 14.4443 | 0.0001079 | 118450
31 | 0.05515 | 0.25395 | 0.0365 | 115 | 115000 | 7.2936 | 33.5849 | 0.00027599 | 118450
32 | 0.05515 | 0.25395 | 0.0365 | 115 | 115000 | 7.2936 | 33.5849 | 0.00027599 | 118450
33 | 0.07058 | 0.1999 | 0.0262 | 115 | 115000 | 9.3342 | 26.4374 | 0.00019811 | 118450
34 | 0.03831 | 0.10922 | 0.01427 | 115 | 115000 | 5.0665 | 14.4443 | 0.0001079 | 118450
35 | 0.01192 | 0.079814 | 0.02142 | 115 | 115000 | 1.5764 | 10.5554 | 0.00016197 | 118450
36 | 0.07058 | 0.1999 | 0.0262 | 115 | 115000 | 9.3342 | 26.4374 | 0.00019811 | 118450
37 | 0.00338 | 0.0379 | 0.1407 | 230 | 230000 | 1.788 | 20.0491 | 0.00026597 | 236900
38 | 0.00342 | 0.03787 | 0.1409 | 230 | 230000 | 1.8092 | 20.0332 | 0.00026635 | 236900
39 | 0.030807 | 0.14157 | 0.019939 | 115 | 115000 | 4.0742 | 18.723 | 0.00015077 | 118450
40 | 0.068277 | 0.3171 | 0.044767 | 115 | 115000 | 9.0296 | 41.9362 | 0.0003385 | 118450
41 | 0.06041 | 0.1773 | 0.023017 | 115 | 115000 | 7.9892 | 23.4482 | 0.00017404 | 118450
42 | 0.00746 | 0.0342 | 0.00491 | 115 | 115000 | 0.98658 | 4.5229 | 3.7127e-05 | 118450
43 | 0.00746 | 0.0342 | 0.00491 | 115 | 115000 | 0.98658 | 4.5229 | 3.7127e-05 | 118450
44 | 0.003877 | 0.024998 | 0.05269 | 115 | 115000 | 0.51273 | 3.306 | 0.00039841 | 118450
45 | 0.13695 | 0.39046 | 0.05101 | 115 | 115000 | 18.1116 | 51.6383 | 0.00038571 | 118450
46 | 0.13695 | 0.39046 | 0.05101 | 115 | 115000 | 18.1116 | 51.6383 | 0.00038571 | 118450
47 | 0.048282 | 0.14473 | 0.01844 | 115 | 115000 | 6.3853 | 19.1408 | 0.00013943 | 118450
48 | 0.048282 | 0.14473 | 0.01844 | 115 | 115000 | 6.3853 | 19.1408 | 0.00013943 | 118450
49 | 0.045011 | 0.13463 | 0.017152 | 115 | 115000 | 5.9527 | 17.8043 | 0.00012969 | 118450
50 | 0.02659 | 0.12209 | 0.01755 | 115 | 115000 | 3.5165 | 16.1464 | 0.0001327 | 118450
51 | 0.057758 | 0.26801 | 0.038756 | 115 | 115000 | 7.6385 | 35.4445 | 0.00029305 | 118450
52 | 0.057733 | 0.26804 | 0.038755 | 115 | 115000 | 7.6352 | 35.4482 | 0.00029304 | 118450
53 | 0.034455 | 0.1602 | 0.022626 | 115 | 115000 | 4.5567 | 21.1861 | 0.00017109 | 118450
54 | 0.034426 | 0.16027 | 0.022626 | 115 | 115000 | 4.5528 | 21.1952 | 0.00017109 | 118450
55 | 0.071977 | 0.20521 | 0.02682 | 115 | 115000 | 9.519 | 27.1389 | 0.0002028 | 118450
56 | 0.071977 | 0.20521 | 0.02682 | 115 | 115000 | 9.519 | 27.1389 | 0.0002028 | 118450
57 | 0.06103 | 0.17399 | 0.02274 | 115 | 115000 | 8.0712 | 23.0102 | 0.00017195 | 118450
58 | 0.06103 | 0.17399 | 0.02274 | 115 | 115000 | 8.0712 | 23.0102 | 0.00017195 | 118450
59 | 0.02257 | 0.17127 | 0.038111 | 230 | 230000 | 11.9395 | 90.6024 | 7.2043e-05 | 236900
60 | 0.02257 | 0.17127 | 0.038111 | 230 | 230000 | 11.9395 | 90.6024 | 7.2043e-05 | 236900
61 | 0.03031 | 0.08642 | 0.01129 | 115 | 115000 | 4.0085 | 11.429 | 8.5369e-05 | 118450
62 | 0.03031 | 0.08642 | 0.01129 | 115 | 115000 | 4.0085 | 11.429 | 8.5369e-05 | 118450
63 | 0.002067 | 0.022997 | 0.086781 | 230 | 230000 | 1.0934 | 12.1654 | 0.00016405 | 236900
64 | 0.002055 | 0.023026 | 0.086771 | 230 | 230000 | 1.0871 | 12.1808 | 0.00016403 | 236900
65 | 0.08951 | 0.26065 | 0.03454 | 115 | 115000 | 11.8377 | 34.471 | 0.00026117 | 118450
66 | 0.08951 | 0.26065 | 0.03454 | 115 | 115000 | 11.8377 | 34.471 | 0.00026117 | 118450
67 | 0.04893 | 0.13874 | 0.01812 | 115 | 115000 | 6.471 | 18.3484 | 0.00013701 | 118450
68 | 0.04893 | 0.13874 | 0.01812 | 115 | 115000 | 6.471 | 18.3484 | 0.00013701 | 118450
69 | 0.022461 | 0.17119 | 0.088181 | 115 | 115000 | 2.9705 | 22.6399 | 0.00066678 | 118450
70 | 0.007093 | 0.054234 | 0.11173 | 230 | 230000 | 3.7522 | 28.6898 | 0.00021121 | 236900
71 | 0.007107 | 0.054218 | 0.11173 | 230 | 230000 | 3.7596 | 28.6813 | 0.00021121 | 236900
72 | 0.044699 | 0.20828 | 0.029353 | 115 | 115000 | 5.9114 | 27.5448 | 0.00022195 | 118450
73 | 0.03263 | 0.1473 | 0.02057 | 115 | 115000 | 4.3153 | 19.4804 | 0.00015554 | 118450
74 | 0.007107 | 0.054218 | 0.11173 | 230 | 230000 | 3.7596 | 28.6813 | 0.00021121 | 236900
75 | 0.007093 | 0.054234 | 0.11173 | 230 | 230000 | 3.7522 | 28.6898 | 0.00021121 | 236900
76 | 0.014095 | 0.10705 | 0.22143 | 230 | 230000 | 7.4563 | 56.6289 | 0.00041857 | 236900
77 | 0.02214 | 0.10061 | 0.01476 | 115 | 115000 | 2.928 | 13.3057 | 0.00011161 | 118450
78 | 0.037498 | 0.1692 | 0.02367 | 115 | 115000 | 4.9591 | 22.3766 | 0.00017898 | 118450
79 | 0.037498 | 0.1692 | 0.02367 | 115 | 115000 | 4.9591 | 22.3766 | 0.00017898 | 118450
80 | 0.041262 | 0.19182 | 0.027179 | 115 | 115000 | 5.4569 | 25.3675 | 0.00020551 | 118450
81 | 0.049187 | 0.22884 | 0.03233 | 115 | 115000 | 6.505 | 30.2644 | 0.00024446 | 118450
82 | 0.049187 | 0.22884 | 0.03233 | 115 | 115000 | 6.505 | 30.2644 | 0.00024446 | 118450
83 | 0.07912 | 0.22866 | 0.03067 | 115 | 115000 | 10.4636 | 30.2403 | 0.00023191 | 118450
84 | 0.032219 | 0.09577 | 0.01215 | 115 | 115000 | 4.261 | 12.6656 | 9.1871e-05 | 118450
85 | 0.05476 | 0.16327 | 0.02054 | 115 | 115000 | 7.242 | 21.5925 | 0.00015531 | 118450
86 | 0.05139 | 0.1484 | 0.01989 | 115 | 115000 | 6.7963 | 19.6259 | 0.0001504 | 118450
87 | 0.09742 | 0.27774 | 0.03629 | 115 | 115000 | 12.8838 | 36.7311 | 0.0002744 | 118450
88 | 0.007114 | 0.049324 | 0.01238 | 115 | 115000 | 0.94083 | 6.5231 | 9.3611e-05 | 118450
89 | 0.007114 | 0.049325 | 0.01238 | 115 | 115000 | 0.94083 | 6.5232 | 9.3611e-05 | 118450
90 | 0.03399 | 0.15812 | 0.02229 | 115 | 115000 | 4.4952 | 20.9114 | 0.00016854 | 118450
91 | 0.034022 | 0.15809 | 0.02229 | 115 | 115000 | 4.4994 | 20.9069 | 0.00016854 | 118450
92 | 0.0034 | 0.022833 | 0.00612 | 115 | 115000 | 0.44965 | 3.0197 | 4.6276e-05 | 118450
93 | 0.003409 | 0.022822 | 0.00612 | 115 | 115000 | 0.45084 | 3.0182 | 4.6276e-05 | 118450
94 | 0.050967 | 0.15223 | 0.01907 | 115 | 115000 | 6.7404 | 20.132 | 0.0001442 | 118450
95 | 5.8e-05 | 0.000385 | 0.000103 | 115 | 115000 | 0.0076705 | 0.050916 | 7.7883e-07 | 118450
96 | 5.7e-05 | 0.000386 | 0.000103 | 115 | 115000 | 0.0075383 | 0.051049 | 7.7883e-07 | 118450
97 | 0.00787 | 0.04884 | 0.0947 | 230 | 230000 | 4.1632 | 25.8364 | 0.00017902 | 236900
98 | 0.00784 | 0.04887 | 0.09457 | 230 | 230000 | 4.1474 | 25.8522 | 0.00017877 | 236900
99 | 0.004765 | 0.036424 | 0.074846 | 230 | 230000 | 2.5207 | 19.2683 | 0.00014149 | 236900
100 | 0.004774 | 0.036402 | 0.07485 | 230 | 230000 | 2.5254 | 19.2567 | 0.00014149 | 236900
101 | 0.000498 | 0.008542 | 0.05418 | 230 | 230000 | 0.26344 | 4.5187 | 0.00010242 | 236900
102 | 0.000498 | 0.008542 | 0.05418 | 230 | 230000 | 0.26344 | 4.5187 | 0.00010242 | 236900
103 | 0.01414 | 0.10845 | 0.22203 | 230 | 230000 | 7.4801 | 57.37 | 0.00041972 | 236900
104 | 0.08174 | 0.30437 | 0.12353 | 230 | 230000 | 43.2405 | 161.0123 | 0.00023352 | 236900
105 | 0.00901 | 0.06933 | 0.14108 | 230 | 230000 | 4.7663 | 36.6756 | 0.00026669 | 236900
106 | 0.009 | 0.06933 | 0.14109 | 230 | 230000 | 4.761 | 36.6756 | 0.00026671 | 236900
107 | 0.000929 | 0.018118 | 1.882 | 500 | 500000 | 2.3225 | 45.295 | 0.00075279 | 515000
108 | 0.000919 | 0.018143 | 1.8817 | 500 | 500000 | 2.2975 | 45.3575 | 0.00075269 | 515000
109 | 0.047573 | 0.15024 | 0.02216 | 115 | 115000 | 6.2915 | 19.8692 | 0.00016756 | 118450
110 | 0.046704 | 0.14736 | 0.02174 | 115 | 115000 | 6.1766 | 19.4885 | 0.00016439 | 118450
111 | 0.027746 | 0.12907 | 0.018207 | 115 | 115000 | 3.6694 | 17.0691 | 0.00013767 | 118450
112 | 0.013881 | 0.064516 | 0.036419 | 115 | 115000 | 1.8358 | 8.5322 | 0.00027538 | 118450
113 | 0.000289 | 0.002007 | 0.0039 | 230 | 230000 | 0.15288 | 1.0617 | 7.3724e-06 | 236900
114 | 0.000289 | 0.002007 | 0.0039 | 230 | 230000 | 0.15288 | 1.0617 | 7.3724e-06 | 236900
115 | 0.041289 | 0.19175 | 0.027183 | 115 | 115000 | 5.4605 | 25.3595 | 0.00020554 | 118450
116 | 0.01807 | 0.081569 | 0.01139 | 115 | 115000 | 2.3898 | 10.7875 | 8.6125e-05 | 118450
117 | 0.052732 | 0.15514 | 0.0202 | 115 | 115000 | 6.9738 | 20.5178 | 0.00015274 | 118450
118 | 0.052762 | 0.15511 | 0.0202 | 115 | 115000 | 6.9778 | 20.5136 | 0.00015274 | 118450
119 | 0.00526 | 0.03458 | 0.00887 | 115 | 115000 | 0.69564 | 4.5732 | 6.707e-05 | 118450
120 | 0.00526 | 0.03458 | 0.00887 | 115 | 115000 | 0.69564 | 4.5732 | 6.707e-05 | 118450
121 | 0.003883 | 0.024992 | 0.05268 | 115 | 115000 | 0.51353 | 3.3052 | 0.00039834 | 118450
122 | 0.000491 | 0.003296 | 0.000885 | 115 | 115000 | 0.064935 | 0.4359 | 6.6919e-06 | 118450
123 | 0.000492 | 0.003293 | 0.000885 | 115 | 115000 | 0.065067 | 0.4355 | 6.6919e-06 | 118450
124 | 0.004429 | 0.028442 | 0.05943 | 230 | 230000 | 2.3429 | 15.0458 | 0.00011234 | 236900
125 | 0.004435 | 0.028435 | 0.05944 | 230 | 230000 | 2.3461 | 15.0421 | 0.00011236 | 236900
126 | 0.003877 | 0.024998 | 0.05269 | 230 | 230000 | 2.0509 | 13.2239 | 9.9603e-05 | 236900
127 | 0.003883 | 0.024992 | 0.05268 | 230 | 230000 | 2.0541 | 13.2208 | 9.9584e-05 | 236900
128 | 0.001918 | 0.021485 | 0.08096 | 230 | 230000 | 1.0146 | 11.3656 | 0.00015304 | 236900
129 | 0.001928 | 0.021474 | 0.08097 | 230 | 230000 | 1.0199 | 11.3597 | 0.00015306 | 236900
130 | 0.00099 | 0.011062 | 0.04173 | 230 | 230000 | 0.52371 | 5.8518 | 7.8885e-05 | 236900
131 | 0.000986 | 0.011071 | 0.041733 | 230 | 230000 | 0.52159 | 5.8566 | 7.889e-05 | 236900
132 | 0.00999 | 0.07442 | 0.15199 | 230 | 230000 | 5.2847 | 39.3682 | 0.00028732 | 236900
133 | 0.00966 | 0.07193 | 0.14691 | 230 | 230000 | 5.1101 | 38.051 | 0.00027771 | 236900
134 | 0.00966 | 0.07193 | 0.14691 | 230 | 230000 | 5.1101 | 38.051 | 0.00027771 | 236900
135 | 0.00999 | 0.07442 | 0.15199 | 230 | 230000 | 5.2847 | 39.3682 | 0.00028732 | 236900
136 | 0.00011 | 0.001976 | 0.011254 | 230 | 230000 | 0.05819 | 1.0453 | 2.1274e-05 | 236900
137 | 0.000111 | 0.001974 | 0.011266 | 230 | 230000 | 0.058719 | 1.0442 | 2.1297e-05 | 236900
138 | 0.036976 | 0.16941 | 0.024587 | 115 | 115000 | 4.8901 | 22.4047 | 0.00018591 | 118450
139 | 0.036976 | 0.16941 | 0.024587 | 115 | 115000 | 4.8901 | 22.4047 | 0.00018591 | 118450
140 | 0.06032 | 0.16449 | 0.02488 | 115 | 115000 | 7.9773 | 21.7538 | 0.00018813 | 118450
141 | 0.001153 | 0.022493 | 0.13853 | 500 | 500000 | 2.8825 | 56.2325 | 5.5411e-05 | 515000
142 | 0.001141 | 0.022523 | 0.13822 | 500 | 500000 | 2.8525 | 56.3075 | 5.5286e-05 | 515000
143 | 0.000886 | 0.017276 | 1.7961 | 500 | 500000 | 2.215 | 43.19 | 0.00071844 | 515000
144 | 0.000876 | 0.017299 | 1.7959 | 500 | 500000 | 2.19 | 43.2475 | 0.00071835 | 515000
145 | 0.022117 | 0.066149 | 0.008428 | 115 | 115000 | 2.925 | 8.7482 | 6.3728e-05 | 118450
146 | 0.022895 | 0.068476 | 0.008724 | 115 | 115000 | 3.0279 | 9.056 | 6.5966e-05 | 118450
147 | 0.00053 | 0.010325 | -0.027686 | 500 | 500000 | 1.325 | 25.8125 | -1.1074e-05 | 515000
148 | 0.000524 | 0.010341 | -0.027827 | 500 | 500000 | 1.31 | 25.8525 | -1.1131e-05 | 515000
149 | 0.000486 | 0.009587 | -0.10473 | 500 | 500000 | 1.215 | 23.9675 | -4.1891e-05 | 515000
150 | 0.000491 | 0.009574 | -0.1046 | 500 | 500000 | 1.2275 | 23.935 | -4.1838e-05 | 515000
151 | 0.000609 | 0.012011 | 0.14691 | 500 | 500000 | 1.5225 | 30.0275 | 5.8764e-05 | 515000
152 | 0.000615 | 0.011995 | 0.14708 | 500 | 500000 | 1.5375 | 29.9875 | 5.883e-05 | 515000
153 | 0.001525 | 0.02163 | -0.01444 | 500 | 500000 | 3.8125 | 54.075 | -5.776e-06 | 515000
154 | 0.001535 | 0.021605 | -0.01419 | 500 | 500000 | 3.8375 | 54.0125 | -5.676e-06 | 515000
155 | 0.001966 | 0.015509 | 0.037131 | 230 | 230000 | 1.04 | 8.2043 | 7.0191e-05 | 236900
156 | 0.001962 | 0.015513 | 0.037117 | 230 | 230000 | 1.0379 | 8.2064 | 7.0164e-05 | 236900
157 | 0.015798 | 0.11999 | 0.25735 | 230 | 230000 | 8.3571 | 63.4731 | 0.00048648 | 236900
158 | 0.015798 | 0.11999 | 0.25735 | 230 | 230000 | 8.3571 | 63.4731 | 0.00048648 | 236900
159 | 0.001515 | 0.021511 | -0.58202 | 500 | 500000 | 3.7875 | 53.7775 | -0.00023281 | 515000
160 | 0.001532 | 0.02147 | -0.5816 | 500 | 500000 | 3.83 | 53.675 | -0.00023264 | 515000
161 | 0.00493 | 0.02262 | 0.00325 | 115 | 115000 | 0.65199 | 2.9915 | 2.4575e-05 | 118450
162 | 0.02214 | 0.10061 | 0.01476 | 115 | 115000 | 2.928 | 13.3057 | 0.00011161 | 118450
163 | 0.004231 | 0.032258 | 0.066444 | 230 | 230000 | 2.2382 | 17.0645 | 0.0001256 | 236900
164 | 0.004223 | 0.032276 | 0.066441 | 230 | 230000 | 2.234 | 17.074 | 0.0001256 | 236900
165 | 0.015644 | 0.11928 | 0.24569 | 230 | 230000 | 8.2757 | 63.0996 | 0.00046444 | 236900
166 | 0.015616 | 0.11935 | 0.24568 | 230 | 230000 | 8.2609 | 63.1351 | 0.00046442 | 236900
167 | 0.003832 | 0.048107 | 0.14424 | 230 | 230000 | 2.0271 | 25.4486 | 0.00027267 | 236900
168 | 0.003854 | 0.048053 | 0.14426 | 230 | 230000 | 2.0388 | 25.42 | 0.0002727 | 236900
169 | 0.008054 | 0.06708 | 0.007327 | 115 | 115000 | 1.0651 | 8.8713 | 5.5403e-05 | 118450
170 | 0.008075 | 0.067028 | 0.007328 | 115 | 115000 | 1.0679 | 8.8645 | 5.541e-05 | 118450
171 | 0.04012 | 0.18399 | 0.026707 | 115 | 115000 | 5.3059 | 24.3321 | 0.00020194 | 118450
172 | 0.040172 | 0.18386 | 0.026709 | 115 | 115000 | 5.3127 | 24.3156 | 0.00020196 | 118450
173 | 0.003788 | 0.074861 | 0.34725 | 230 | 230000 | 2.0039 | 39.6015 | 0.00065643 | 236900
174 | 0.003838 | 0.074735 | 0.34726 | 230 | 230000 | 2.0303 | 39.5348 | 0.00065645 | 236900
175 | 0.049172 | 0.14255 | 0.019058 | 115 | 115000 | 6.503 | 18.8522 | 0.00014411 | 118450
176 | 0.049145 | 0.14258 | 0.01906 | 115 | 115000 | 6.4994 | 18.8562 | 0.00014412 | 118450
177 | 0.075884 | 0.22299 | 0.028891 | 115 | 115000 | 10.0357 | 29.4902 | 0.00021846 | 118450
178 | 0.019634 | 0.13124 | 0.035529 | 115 | 115000 | 2.5966 | 17.3565 | 0.00026865 | 118450
179 | 0.019634 | 0.13124 | 0.035529 | 115 | 115000 | 2.5966 | 17.3565 | 0.00026865 | 118450
180 | 0.00085 | 0.00389 | 0.00056 | 115 | 115000 | 0.11241 | 0.51445 | 4.2344e-06 | 118450
181 | 0.00085 | 0.00389 | 0.00056 | 115 | 115000 | 0.11241 | 0.51445 | 4.2344e-06 | 118450
182 | 0.001996 | 0.031677 | 0.76239 | 500 | 500000 | 4.99 | 79.1925 | 0.00030496 | 515000
183 | 0.001996 | 0.031677 | 0.76239 | 500 | 500000 | 4.99 | 79.1925 | 0.00030496 | 515000
184 | 0.008813 | 0.066944 | 0.1385 | 230 | 230000 | 4.6621 | 35.4134 | 0.00026181 | 236900

## MPS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM017_ver01.0
Reference Number: TH024
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 21559.7894 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for grid |  |  | N/A | 0.5664 | tCO2/MWh | EFGrid
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 300442.5187 | tCO2/p | REp
|  | Reference transmission line loss at transmission lines in the project area X during the period p |  | N/A | 530442.3 | MWh/p | PLRE,X,lines,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 278882.7293 | tCO2/p | PEp
|  | Project transmission line loss at transmission lines in the project area X during the period p |  | N/A | 492377.7 | MWh/p | PLPJ,X,lines,p
[List of Default Values]

## MSS
Monitoring Spreadsheet: JCM_TH_AM017_ver01.0
Reference Number: TH024
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| General Manager (Stationed in Japan) | Responsible for project management
| Project Manager (Stationed in Japan) | Responsible for OPENVQ system manegement in Japan and monitoring.
| Project Manager (Stationed in Thailand) | Responsible for OPENVQ system manegement in Thailand and monitoring.
| Chief of system operation (Stationed in Japan) | The person for operating OPENVQ system, monitoring OPENVQ system condition, first responder in case of trouble in Japan.
| Chief of system operation (Stationed in Thailand) | The person for operating OPENVQ system, monitoring OPENVQ system condition, first responder in case of trouble in Thailand.
| Data director (Stationed in Japan) | The person to check the data from OPENVQ system for monitoring tasks.

## MRS(input)
Monitoring Spreadsheet: JCM_TH_AM017_ver01.0
Reference Number: TH024
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | N | Number of transmission lines in the project area X |  | - | Option C | Monitored data | The value is counted in the OPENVQ system. | Continuously
|  | (2) | Pk,i,t | Active power at the bus k of transmission line i at the time t | - | W | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at pre-determined interval are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
|  | (3) | Vk,i,t | Voltage measured at the bus k of transmission line i at the time t | - | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at pre-determined interval are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
|  | (4) | Vl,i,t | Voltage measured at the bus l of transmission line i at the time t | - | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at pre-determined interval are considered to identify power grid condition on OPENVQ system. An electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
|  | (5) | Qk,i,t | Reactive power at the bus k of transmission line i at the time t | - | var | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system are sent to OPENVQ system automatically. 5) Measurands at pre-determined interval are considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and properly managed in line with the procedures established by EGAT. | Continuously
|  | - | PLRE,X,lines,p | Reference transmission line loss at transmission lines in the project area X during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | PLPJ,X,lines,p | Project transmission line loss at transmission lines in the project area X during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | PLRE,linei,p | Reference transmission line loss at transmission line i during the period p | - | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | PLRE,linei,t | Reference transmission line loss at transmission line i at the time t | - | W | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | QRE,k,i,t | Reference reactive power at the bus k of transmission line i at the time t | - | var | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | VRE,l,i,t | Reference voltage at the bus l of transmission line i at the time t | - | V | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data in line with the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | PLPJ,linei,p | Project transmission line loss at transmission line i during the period p | - | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
|  | - | PLPJ,linei,t | Project transmission line loss at transmission line i at the time t | - | W | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFGrid |  | CO2 emission factor for grid |  | 0.5664 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization, unless otherwise instructed by the Joint Committee. |  |  | 0
| Ratiomode | Ratiomode | Mode value of Ratiok of Vk,i to the base voltage Vbase,i of transmission line i |  | 1.03 | - | Calculated based on the procedure described in F.2. of the methodology. |  |  | 0
| Ri | Ri | Resistance of transmission line i |  | 0 | Ω | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| Xi | Xi | Reactance of transmission line i |  | 0 | Ω | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| Bi | Bi | Susceptance of transmission line i |  | 0 | S | Calculated by electromagnetics based on the configuration characteristics like tower geometry, conductor types, number, phasing and ground condition of circuits of overhead transmission line i which are obtained from EGAT. The calculations are performed using a general-purpose calculation program package. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| T | T | Measurement interval |  | 5 | min | Predetermined measurement interval |  |  | 0
| Vbase,i | Vbase,i | Base voltage of transmission line i |  | 0 | V | Specification of transmission line i |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
| VRE,k,i | VRE,k,i | Reference voltage at the bus k of transmission line i |  | 0 | V | Calculated based on the procedure described in F.2. of the methodology. |  |  | Described in the separate sheet "Value Vbase,i,Ri,Xi,Bi,VRE,k,i"
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period | CO2 emission reductions |  | Units
|  | 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM017_ver01.0
Reference Number: TH024
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for grid |  |  | N/A | 0.5664 | tCO2/MWh | EFGrid
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference transmission line loss at transmission lines in the project area X during the period p |  | N/A | 0 | MWh/p | PLRE,X,lines,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project transmission line loss at transmission lines in the project area X during the period p |  | N/A | 0 | MWh/p | PLPJ,X,lines,p
[List of Default Values]