## MPS(input)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | Continuously | Input on "MPS (input_separate)"
| (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p |  | mass or weight/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company. | Continuously | for option b
| (3) | EGPJ,p | The amount of electricity generated during the monitoring period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Specification of measuring equipment: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | Continuously | for option b
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | [For grid electricity] CO2 emission factor for consumed electricity |  |  | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated |  |  | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  |  | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec | Power generation efficiency |  |  | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel | Net calorific value of consumed fuel |  |  | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel | CO2 emission factor of consumed fuel |  |  | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## MPS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
|  | Parameters to be monitored ex post |  |  | Project-specific parameters to be fixed ex ante | [11 empty] | Ex-ante estimation of emissions
Parameters | Chiller i | ECPJ,i,p | FCPJ,p | EGPJ,p | EFelec | EFelec | EFelec | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | ηelec | NCVfuel | EFfuel | REi,p | PEi,p | ERi,p
Description of data | Project chiller No. | Power consumption of project chiller i during the period p | The amount of fuel input for power generation during monitoring period p | The amount of electricity generated during the monitoring period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Power generation efficiency | Net calorific value of consumed fuel | CO2 emission factor of consumed fuel | Reference emissions of project chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | mass or weight/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | % | GJ/mass or weight | tCO2/GJ | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 12 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 16 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 17 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 18 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 19 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | 0 | 0

## MPS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
COPRE,i for inverter type
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## MSS
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role

## MRS(input)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | Continuously | Input on "MRS (input_separate)"
|  | (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p |  | mass or weight/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company. | Continuously | for option b
|  | (3) | EGPJ,p | The amount of electricity generated during the monitoring period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Specification of measuring equipment: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | Continuously | for option b
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | [For grid electricity] CO2 emission factor for consumed electricity |  |  | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated |  |  | Calculated
| EFelec |  | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  |  | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i |  | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i |  | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i |  | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i |  | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i |  | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec |  | Power generation efficiency |  |  | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel |  | Net calorific value of consumed fuel |  |  | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel |  | CO2 emission factor of consumed fuel |  |  | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## MRS(input_separate)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
|  | Parameters monitored ex post |  |  | Project-specific parameters fixed ex ante | [11 empty] | Ex-post calculation of emissions
Parameters | Chiller i | ECPJ,i,p | FCPJ,p | EGPJ,p | EFelec | EFelec | EFelec | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | ηelec | NCVfuel | EFfuel | REi,p | PEi,p | ERi,p
Description of data | Project chiller No. | Power consumption of project chiller i during the period p | The amount of fuel input for power generation during monitoring period p | The amount of electricity generated during the monitoring period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Power generation efficiency | Net calorific value of consumed fuel | CO2 emission factor of consumed fuel | Reference emissions of project chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | mass or weight/p | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | % | GJ/mass or weight | tCO2/GJ | tCO2/p | tCO2/p | tCO2/p
Monitored /estimated values | 1 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 2 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 3 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 4 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 5 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 6 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 7 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 8 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 9 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 10 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 11 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 12 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 13 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 14 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 15 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 16 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 17 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 18 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 19 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| 20 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | 0 | 0

## MRS(calc_process)
Monitoring Spreadsheet: JCM_TH_AM003_ver01.0
Reference Number:
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
COPRE,i for inverter type
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius