## PMS(input)
JCM_TH_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,DV,i,j,k,p | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | - | MWh/p | Option C | Monitored data | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is replaced or calibrated at an interval following the regulations in the country in which the electricity meter is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the electrical power meter has been prepared by the time of installation. | Continuously | Input on "PMS (input_separate)"
| (2) | FCPJ,p | The amount of fuel input for power generation during monitoring period p | 0 | mass or weight/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company. | Continuously | for option c)
| (3) | EGPJ,p | The amount of electricity generated during the monitoring period p | 0 | MWh/p | Option C | Monitored data | On-site measurement by measuring equipments. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement. 2) Meter is certified in compliance with national/international standards on electrical power meter. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The electrical power meter is replaced or calibrated at an interval following the regulations in the country in which the electricity meter is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the electrical power meter has been prepared by the time of installation. | Continuously | for option c)
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec,k | [For grid electricity] CO2 emission factor for consumed electricity |  | 0 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated. |  |  | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | 0 | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| AFRRE,j,k | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document of the cleanroom. |  |  | Calculated
| AFRPJ,j,k | Airflow rate of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | m3/s | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "PMS (input_separate)"
| Pd,RE,j,k | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | 1200 | Pa | Hearing survey with manufacturer of mixing ventilation air conditioning unit. |  |  | Default value
| Pd,PJ,j,k | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k |  | - | Pa | Design document or specification document of the displacement ventilation air conditioning unit. |  |  | Input on "PMS (input_separate)"
| Vcr,j,k | Volume of the cleanroom j in the project factory k |  | - | m3 | Design document of the cleanroom. |  |  | Input on "PMS (input_separate)"
| Tvent,j,k | Number of times of ventilation required for the cleanroom j in the project factory k |  | - | times/h | Multiple documents published on the web. The default value is determined from the table corresponding to the airborne particulate cleanliness class required for the cleanroom. |  |  | Input on "PMS (input_separate)" Select from default values
| ηelec | Power generation efficiency |  | 0 | % | Specification of the captive power generation system provided by the manufacturer
| NCVfuel | Net calorific value of consumed fuel |  | 0 | GJ/mass or weight | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| EFfuel | CO2 emission factor of consumed fuel |  | 0 | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## PMS(input_separate)
Calculation of reference emissions
| Identification numbers |  |  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [9 empty] | Ex-ante estimation of emissions
Parameters | i | j | k | ECPJ,AC,i,j,k,p | EFelec | EFelec | EFelec | EFelec | AFRRE,j,k | AFRPJ,i,j,k | Pd,RE,j,k | Pd,PJ,j,k | Vcr,j,k | Tvent,j,k | REi,p
Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Airflow rate of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Airflow rate of project displacement ventilation air conditioning unit i supplying air to cleanroom j in the project factory k | Discharge pressure of reference mixing ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Discharge pressure of project displacement ventilation air conditioning unit(s) supplying air to cleanroom j in the project factory k | Volume of the cleanroom j in the project factory k | Number of times of ventilation required for the cleanroom j in the project factory k | Reference emissions of the reference mixing ventilation air conditioning unit i during the period p
Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | m3/s | m3/s | Pa | Pa | m3 | times/h | tCO2/p
Estimated values | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0 | 0
| 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0 | 80
| 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0 | 40
| 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 17 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 18 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 19 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| 20 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0.0
| Total | - | - | - | - | - | - | - | - | - | - | - | - | - | 0
Calculation of project emissions
| Identification numbers |  |  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante |  |  |  | Ex-ante estimation of emissions
Parameters | i | j | k | ECPJ,DV,i,j,k,p | EFelec | EFelec | EFelec | EFelec | PEi,p
Description of data | Identification number of the displacement ventilation air conditioning unit | Identification number of the cleanroom | Identification number of the factory | The amount of power consumption by the project displacement ventilation air conditioning unit i in cleanroom j of the project factory k during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity Option c | Project emissions of the project displacement ventilation air conditioning unit i during the period p
Units | - | - | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/p
Estimated values | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 16 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 17 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 18 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 19 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| 20 |  |  | 0 | 0 | 0 | 0 | 0 | 0.0
| Total |  |  | - | - | - | - | - | 0

## PMS(calc_process)
JCM_TH_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | Number of times of ventilation required for the cleanroom | ISO 14644-1:2015 | FED-STD-209E | Tvent,j,k
|  |  |  | Class 6 | 1000 | 80
|  |  |  | Class 7 | 10000 | 40
|  |  | Discharge pressure of reference mixing ventilation air conditioning unit |  | 1200 | Pa