## PMS(input)
JCM_TH_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| N/A | PLRE,X,lines,p | Reference transmission line loss at transmission lines in the project area X during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data according to the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | PLPJ,X,lines,p | Project transmission line loss at transmission lines in the project area X during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | PLRE,linei,p | Reference transmission line loss at transmission line i during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data according to the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | N | Number of transmission lines in the project area X |  | - | Option C | Monitored data | The value is counted in the OPENVQ system. | Continuously
| N/A | PLRE,linei,t | Reference transmission line loss at transmission line i at the time t |  | W | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data according to the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | Pk,i,t | Active power at the bus k of transmission line i at the time t |  | W | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system is sent to OPENVQ system automatically. 5) Measurands at pre-determined interval is considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and properly managed according to the procedures established by EGAT. | Continuously
| N/A | Vk,i,t | Voltage measured at the bus k of transmission line i at the time t |  | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system is sent to OPENVQ system automatically. 5) Measurands at pre-determined interval is considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and properly managed according to the procedures established by EGAT. | Continuously
| N/A | Vl,i,t | Voltage measured at the bus l of transmission line i at the time t |  | V | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system is sent to OPENVQ system automatically. 5) Measurands at pre-determined interval is considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and properly managed according to the procedures established by EGAT. | Continuously
| N/A | Qk,i,t | Reactive power at the bus k of transmission line i at the time t |  | var | Option C | Monitored data | Measured by three-phase electrical power meter by following method: 1) An electrical power meter is connected to the secondary side of an instrument transformer. 2) All transmission lines have the electrical meters at both sending side and receiving side. 3) Measurands are sent to SCADA system to retrieve to identify the power grid condition. 4) All recording data retrieved by SCADA system is sent to OPENVQ system automatically. 5) Measurands at pre-determined interval is considered to identify power grid condition on OPENVQ system. Electrical power meter has been in place before the introduction of OPENVQ and has been properly managed according to the procedures established by EGAT. | Continuously
| N/A | QRE,k,i,t | Reference reactive power at the bus k of transmission line i at the time t |  | var | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data according to the procedure described in F.2. of the methodology. The monitored data of each transmission line, active power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | VRE,l,i,t | Reference voltage at the bus l of transmission line i at the time t |  | V | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data according to the procedure described in F.2. of the methodology. The monitored data of each transmission line, reactive power and reactance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
| N/A | PLPJ,linei,p | Project transmission line loss at transmission line i during the period p |  | MWh/p | Option C | Monitored data | The value is calculated in the OPENVQ system based on the monitored data. The monitored data of each transmission line, active power, reactive power, voltage, resistance, reactance, and susceptance, are collected and recorded at the central control panel of respective regional control center. The monitored data is sent to OPENVQ system automatically, and constantly. The calculation is conducted by sampling the continuously monitored data once every five minitues. | Continuously
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFGrid | CO2 emission factor for grid |  |  | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Thailand”, endorsed by Thailand Greenhouse Gas Management Organization, unless otherwise instructed by the Joint Committee.
| Ratiomode | Mode value of Ratiok of Vk,i to the base voltage Vbase,i of transmission line i |  |  | - | Calculated according to the procedure described in F.2. of the methodology.
| Ri | Resistance of transmission line i |  |  | Ω | The constant value of equivalent circuit which represents the condition of transmission line i
| Xi | Reactance of transmission line i |  |  | Ω | The constant value of equivalent circuit which represents the condition of transmission line i
| Bi | Susceptance of transmission line i |  |  | S | The constant value of equivalent circuit which represents the condition of transmission line i
| T | Measurement interval |  |  | min | Pre determined measurement interval
| Vbase,i | Base voltage of transmission line i |  |  | V | Specification of transmission line i
| VRE,k,i | Reference voltage at the bus k of transmission line i |  |  | V | Calculated according to the procedure described in F.2. of the methodology.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## PMS(calc_process)
JCM_TH_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for grid |  |  | N/A | 0 | tCO2/MWh | EFGrid
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference transmission line loss at transmission lines in the project area X during the period p |  | N/A | 0 | MWh/p | PLRE,X,lines,p
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project transmission line loss at transmission lines in the project area X during the period p |  | N/A | 0 | MWh/p | PLPJ,X,lines,p
[List of Default Values]
|  |  | CO2 emission factor for grid |  | tCO2/MWh