## MPS(input)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| 1 | ECPJ,i,outdoor,p | Electricity consumption of outdoor unit of project air conditioning system i during the period p | - | MWh/p | Option C | Monitored data | - Measuring equipment is installed in each outdoor unit of air conditioning system to measure power consumption. - Measured data is automatically transmitted to the server for recording. - data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. - in case a calibration certificate issued by an entity accredited under national/international standards is not provided, such Measuring equipment is required to be calibrated. | Continuously | Monitored values are input on "MPS(input_each system)" sheet
| 2 | ECPJ,indoor,p | Total electricity consumption of indoor units of project air conditioning system during the period p | 253 | MWh/p | Option C | Monitored data | Monitoring is conducted with any of the following methods: [Method 1: Measuring equipment] - Measuring equipment is installed to measure power consumption by air conditioning system. - Measured data is automatically transmitted to the server for recording. - Data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. - In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. | Continuously | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor for consumed electricity. When captive power generation is not available at the project site, then the most recent Vietnamese national grid emission factor [EFgrid] available at the time of validation is applied as [EFelec] and fixed for the monitoring period thereafter. When captive power generation is available at the project site, then [EFelec] is conservatively selected as below and fixed for the monitoring period thereafter: EFelec = min(EFgrid, EFcaptive) EFcaptive = 0.8 tCO2/MWh* *The most recent emission factor available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. |  | 0.5657 | tCO2/MWh | [EFgrid] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology: AMS-I.A |  |  | n/a
| COPPJ,i,outdoor | COP of outdoor unit of project air conditioning system i (Outdoor unit) |  | - | - | Specifications of project air conditioning system for the quotation or factory acceptance test data by manufacturer. |  |  | Values are input on "MPS(input_each system)" sheet
| COPRE,i | COP of reference air conditioning system i (Outdoor Unit + Indoor Unit) |  | - | - | Nominal value available on product catalogs, specification documents or websites, hearing survey. The default values are derived from the result of survey on COP of air conditioning system with non-inverter from manufacturers that have high market share. The default values should be revised if necessary from survey result which is conducted by JC or project participants every three years. The survey should prove the use of clear methodology. |  |  | Values are input on "MPS(input_each system)" sheet
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 935 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(input_each system)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante |  |  | Ex-ante estimation of emissions
Parameters | i | ECPJ,i,outdoor,p | COPPJ,i,outdoor | COPRE,i | EFelec | REi,p | PEi,outdoor,p
Description of data | Identification number of air conditioning system | Electricity consumption of outdoor unit of project air conditioning system i during the period p | COP of outdoor unit of project air conditioning system i | COP of reference air conditioning system i | CO2 emission factor for consumed electricity | Reference emissions by air conditioning system i during the period p | Project emissions by outdoor unit air conditioning system i during the period p
Units | - | MWh/p | - |  | tCO2/MWh | tCO2/p | tCO2/p
Estimated values | 1 | 141.1236 | 4.53 | 2.56 | 0.5657 | 141.2681 | 79.8336
| 2 | 205.7724 | 4.05 | 2.56 | 0.5657 | 184.1571 | 116.4054
| 3 | 205.7724 | 4.05 | 2.56 | 0.5657 | 184.1571 | 116.4054
| 4 | 290.1312 | 3.29 | 2.56 | 0.5657 | 210.9291 | 164.1272
| 5 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 6 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 7 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 8 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 9 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 10 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 11 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 12 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 13 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 14 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 15 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 16 | 192.72 | 4.09 | 2.56 | 0.5657 | 174.1792 | 109.0217
| 17 | 334.632 | 3.27 | 2.56 | 0.5657 | 241.8029 | 189.3013
| 18 |  |  |  | 0.5657 | 0 | 0
| 19 |  |  |  | 0.5657 | 0 | 0
| 20 |  |  |  | 0.5657 | 0 | 0
| 21 |  |  |  | 0.5657 | 0 | 0
| 22 |  |  |  | 0.5657 | 0 | 0
| 23 |  |  |  | 0.5657 | 0 | 0
| 24 |  |  |  | 0.5657 | 0 | 0
| 25 |  |  |  | 0.5657 | 0 | 0
| 26 |  |  |  | 0.5657 | 0 | 0
| 27 |  |  |  | 0.5657 | 0 | 0
| 28 |  |  |  | 0.5657 | 0 | 0
| 29 |  |  |  | 0.5657 | 0 | 0
| 30 |  |  |  | 0.5657 | 0 | 0
| 31 |  |  |  | 0.5657 | 0 | 0
| 32 |  |  |  | 0.5657 | 0 | 0
| 33 |  |  |  | 0.5657 | 0 | 0
| 34 |  |  |  | 0.5657 | 0 | 0
| 35 |  |  |  | 0.5657 | 0 | 0
| 36 |  |  |  | 0.5657 | 0 | 0
| 37 |  |  |  | 0.5657 | 0 | 0
| 38 |  |  |  | 0.5657 | 0 | 0
| 39 |  |  |  | 0.5657 | 0 | 0
| 40 |  |  |  | 0.5657 | 0 | 0
| 41 |  |  |  | 0.5657 | 0 | 0
| 42 |  |  |  | 0.5657 | 0 | 0
| 43 |  |  |  | 0.5657 | 0 | 0
| 44 |  |  |  | 0.5657 | 0 | 0
| 45 |  |  |  | 0.5657 | 0 | 0
| 46 |  |  |  | 0.5657 | 0 | 0
| 47 |  |  |  | 0.5657 | 0 | 0
| 48 |  |  |  | 0.5657 | 0 | 0
| 49 |  |  |  | 0.5657 | 0 | 0
| 50 |  |  |  | 0.5657 | 0 | 0
| Total | - | - | - | - | 3052.4647 | 1974.3335

## MPS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 935.0091 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for consumed electricity. |  |  |  | Electricity | 0.5657 | - | EFelec
| COP of reference air conditioning system i (Outdoor Unit + Indoor Unit) |  |  |  | - | - | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 3052.4647 | tCO2/p | REp
*Calculation for each air conditioning system is detailed in "MPS(input_each system)" sheet
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 2117.4556 | tCO2/p | PEp
|  | Project emissions by outdoor unit |  |  | Electricity | 1974.3335 | tCO2/p | PEoutdoor,p
|  | Project emissions by indoor unit |  |  | Electricity | 143.1221 | tCO2/p | PEindoor,p
|  |  | Total electricity consumption of indoor units of project air conditioning system during the period p |  | Electricity | 253 | MWh/p | ECPJ,indoor,p
|  |  | CO2 emission factor for consumed electricity |  | Electricity | 0.5657 | tCO2/MWh | EFelec
[List of Default Values]
Project-specific parameters to be fixed ex ante
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 14.0 ≤ x < 28.0kW) |  | 2.97
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 28.0 ≤ x < 42.0kW) |  | 2.94
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 42.0 ≤ x < 56.0kW) |  | 2.91
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 56.0 ≤ x ) |  | 2.56

## MSS
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for project planning, implementation, monitoring results and reporting. And appointed to be in charge of approving the archived data after being checked.
| Facility Managers | Appointed to be in charge of monitoring procedure (data collection and storage), including monitoring equipments and calibrations, and training of monitoring personnel. And responsible for corrected the archived data when necessary.
| N/A | N/A
| N/A | N/A
| N/A | N/A
| N/A | N/A
| N/A | N/A

## MRS(input)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitered Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | 1 | ECPJ,i,outdoor,p | Electricity consumption of outdoor unit of project air conditioning system i during the period p | - | MWh/p | Option C | Monitored data | - Measuring equipment is installed in each outdoor unit of air conditioning system to measure power consumption. - Measured data is automatically transmitted to the server for recording. - data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. - in case a calibration certificate issued by an entity accredited under national/international standards is not provided, such Measuring equipment is required to be calibrated. | Continuously | Monitored values are input on "MRS(input_each system)" sheet
|  | 2 | ECPJ,indoor,p | Total electricity consumption of indoor units of project air conditioning system during the period p | 0 | MWh/p | Option C | Monitored data | Monitoring is conducted with any of the following methods: [Method 1: Measuring equipment] - Measuring equipment is installed to measure power consumption by air conditioning system. - Measured data is automatically transmitted to the server for recording. - Data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. - In case a calibration certificate issued by an entity accredited under national/international standards is not provided, such measuring equipment is required to be calibrated. [Method 2: Estimation based on operating hours of indoor unit] - Power consumption of indoor units is estimated from rated power consumption and operating hours of indoor unit with the following equation: ECPJ,i,indoor,p = RPCPJ,i,indoor × HPJ,i,indoor,p RPCPJ,i,indoor: Rated power consumption of indoor unit i HPJ,i,indoor,p: Operating hours of indoor unit i - Measuring equipment is installed in each indoor unit to monitor operating hours. - Measured data is automatically transmitted to the server for recording. - Data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. [Method 3: Estimation based on operating hours of outdoor unit] - Power consumption of indoor units is estimated from rated power consumption of indoor unit and operating hours of connected outdoor unit with the following equation: ECPJ,i,indoor,p = RPCPJ,i,indoor × HPJ,i,outdoor,p RPCPJ,i,indoor: Total rated power consumption of indoor unit connected outdoor unit i HPJ,i,outdoor,p: Operating hours of outdoor unit i - Measuring equipment is installed in each outdoor unit to monitor operating hours. - Measured data is automatically transmitted to the server for recording. - Data recorded in the server is reported and double-checked by a responsible staff on a monthly basis to prevent missing data. | Continuously | n/a
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | CO2 emission factor for consumed electricity. When captive power generation is not available at the project site, then the most recent Vietnamese national grid emission factor [EFgrid] available at the time of validation is applied as [EFelec] and fixed for the monitoring period thereafter. When captive power generation is available at the project site, then [EFelec] is conservatively selected as below and fixed for the monitoring period thereafter: EFelec = min(EFgrid, EFcaptive) EFcaptive = 0.8 tCO2/MWh* *The most recent emission factor available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. |  | 0.5657 | tCO2/MWh | [EFgrid] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology: AMS-I.A |  |  | n/a
| COPPJ,i,outdoor |  | COP of outdoor unit of project air conditioning system i (Outdoor unit) |  | - | - | Specifications of project air conditioning system for the quotation or factory acceptance test data by manufacturer. |  |  | Values are input on "MPS(input_each system)" sheet
| COPRE,i |  | COP of reference air conditioning system i (Outdoor Unit + Indoor Unit) |  | - | - | Nominal value available on product catalogs, specification documents or websites, hearing survey. The default values are derived from the result of survey on COP of air conditioning system with non-inverter from manufacturers that have high market share. The default values should be revised if necessary from survey result which is conducted by JC or project participants every three years. The survey should prove the use of clear methodology. |  |  | Values are input on "MPS(input_each system)" sheet
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(input_each system)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
|  | Parameters monitored ex post | Project-specific parameters fixed ex ante |  |  | Ex-post calculation of emissions
Parameters | i | ECPJ,i,outdoor,p | COPPJ,i,outdoor | COPRE,i | EFelec | REi,p | PEi,outdoor,p
Description of data | Identification number of air conditioning system | Electricity consumption of outdoor unit of project air conditioning system i during the period p | COP of outdoor unit of project air conditioning system i | COP of reference air conditioning system i | CO2 emission factor for consumed electricity | Reference emissions by air conditioning system i during the period p | Project emissions by outdoor unit air conditioning system i during the period p
Units | - | MWh/p | - |  | tCO2/MWh | tCO2/p | tCO2/p
Monitored values | 1 |  | 4.53 | 2.56 | 0.5657 | 0 | 0
| 2 |  | 4.05 | 2.56 | 0.5657 | 0 | 0
| 3 |  | 4.05 | 2.56 | 0.5657 | 0 | 0
| 4 |  | 3.29 | 2.56 | 0.5657 | 0 | 0
| 5 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 6 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 7 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 8 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 9 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 10 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 11 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 12 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 13 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 14 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 15 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 16 |  | 4.09 | 2.56 | 0.5657 | 0 | 0
| 17 |  | 3.27 | 2.56 | 0.5657 | 0 | 0
| 18 |  | 0 | 0 | 0.5657 | 0 | 0
| 19 |  | 0 | 0 | 0.5657 | 0 | 0
| 20 |  | 0 | 0 | 0.5657 | 0 | 0
| 21 |  | 0 | 0 | 0.5657 | 0 | 0
| 22 |  | 0 | 0 | 0.5657 | 0 | 0
| 23 |  | 0 | 0 | 0.5657 | 0 | 0
| 24 |  | 0 | 0 | 0.5657 | 0 | 0
| 25 |  | 0 | 0 | 0.5657 | 0 | 0
| 26 |  | 0 | 0 | 0.5657 | 0 | 0
| 27 |  | 0 | 0 | 0.5657 | 0 | 0
| 28 |  | 0 | 0 | 0.5657 | 0 | 0
| 29 |  | 0 | 0 | 0.5657 | 0 | 0
| 30 |  | 0 | 0 | 0.5657 | 0 | 0
| 31 |  | 0 | 0 | 0.5657 | 0 | 0
| 32 |  | 0 | 0 | 0.5657 | 0 | 0
| 33 |  | 0 | 0 | 0.5657 | 0 | 0
| 34 |  | 0 | 0 | 0.5657 | 0 | 0
| 35 |  | 0 | 0 | 0.5657 | 0 | 0
| 36 |  | 0 | 0 | 0.5657 | 0 | 0
| 37 |  | 0 | 0 | 0.5657 | 0 | 0
| 38 |  | 0 | 0 | 0.5657 | 0 | 0
| 39 |  | 0 | 0 | 0.5657 | 0 | 0
| 40 |  | 0 | 0 | 0.5657 | 0 | 0
| 41 |  | 0 | 0 | 0.5657 | 0 | 0
| 42 |  | 0 | 0 | 0.5657 | 0 | 0
| 43 |  | 0 | 0 | 0.5657 | 0 | 0
| 44 |  | 0 | 0 | 0.5657 | 0 | 0
| 45 |  | 0 | 0 | 0.5657 | 0 | 0
| 46 |  | 0 | 0 | 0.5657 | 0 | 0
| 47 |  | 0 | 0 | 0.5657 | 0 | 0
| 48 |  | 0 | 0 | 0.5657 | 0 | 0
| 49 |  | 0 | 0 | 0.5657 | 0 | 0
| 50 |  | 0 | 0 | 0.5657 | 0 | 0
| Total | - | - | - | - | 0 | 0

## MRS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM006_ver01.0
Reference Number: VN005
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| CO2 emission factor for consumed electricity. |  |  |  | Electricity | 0.5657 | - | EFelec
| COP of reference air conditioning system i (Outdoor Unit + Indoor Unit) |  |  |  | - | - | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | N/A | 0 | tCO2/p | REp
*Calculation for each air conditioning system is detailed in "MRS(input_each system)" sheet
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions by outdoor unit |  |  | Electricity | 0 | tCO2/p | PEoutdoor,p
|  | Project emissions by indoor unit |  |  | Electricity | 0 | tCO2/p | PEindoor,p
|  |  | Total electricity consumption of indoor units of project air conditioning system during the period p |  | Electricity | 0 | MWh/p | ECPJ,indoor,p
|  |  | CO2 emission factor for consumed electricity |  | Electricity | 0.5657 | tCO2/MWh | EFelec
[List of Default Values]
Project-specific parameters to be fixed ex ante
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 14.0 ≤ x < 28.0kW) |  | 2.97
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 28.0 ≤ x < 42.0kW) |  | 2.94
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 42.0 ≤ x < 56.0kW) |  | 2.91
|  |  |  | COP of reference air conditioning system (Outdoor Unit + Indoor Unit) (Cooling capacity 56.0 ≤ x ) |  | 2.56