## AM11_MPS(input)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by power meter. A specification of power meter is provided by its manufacturer, and it states that the accuracy stays within ±2.0% being tested in line with JIS C 1111. There is no statement regarding replacement nor calibration interval recommended by the manufacturer. Therefore, power meters are not a subject of calbration nor replacement during the JCM project period. | Continuously | Input on "MPS (input_separate)"
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor for consumed electricity |  | 0.9185 | tCO2/MWh | [Grid electricity] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [Captive electricity] For the option a) Specification of the captive power generation system provided by the manufacturer (ηelec,CG [%]). CO2 emission factor of the fossil fuel type used in the captive power generation system (EFfuel,CG [tCO2/GJ]) For the option b) Generated and supplied electricity by the captive power generation system (EGPJ,CG,p [MWh/p]). Fuel amount consumed by the captive power generation system (FCPJ,CG,p [mass or volume/p]). Net calorific value (NCVfuel,CG [GJ/mass or volume]) and CO2 emission factor (EFfuel,CG [tCO2/GJ]) of the fuel consumed by the captive power generation system in order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in tables 1.2 and 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 104 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM11_MPS(input_separate)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [5 empty] | Ex-ante estimation of emissions
Parameters | i | ECPJ,i,p | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of project chiller | Power consumption of project chiller i during the period p | CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Reference emissions of reference chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 1216 | 0.9185 | 37 | 7 | 5.69 | 6.22 | 6.22 | 1220.9302 | 1116.896 | 104.0342
| 2 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | 1220.9302 | 1116.896 | 104.0342

## AM11_MPS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 104.0342 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 1220.9302 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 1220.9302 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 1116.896 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 1116.896 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## AM11_MSS
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| HOYA CORPORATION Environment/Occupational Safety and Health Department Group leader | In charge of authorizing the monitoring report.
| HOYA LENS VIETNAM LTD Technical Expert | In charge of approving the archived data after being checked and corrected when necessary and preparation of monitoring report.
| HOYA LENS VIETNAM LTD Facility Manager | In charge of monitoring procedure (data collection and storage), including monitoring equipments and calibrations, and training of monitoring personnel.
| HOYA LENS VIETNAM LTD Facility Staff | In charge of checking the archived data.

## AM11_MRS(input)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by power meter. A specification of power meter is provided by its manufacturer, and it states that the accuracy stays within ±2.0% being tested in line with JIS C 1111. There is no statement regarding replacement nor calibration interval recommended by the manufacturer. Therefore, power meters are not a subject of calbration nor replacement during the JCM project period. | Continuously | Input on "MRS (input_separate)"
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | CO2 emission factor for consumed electricity |  | 0.9185 | tCO2/MWh | [Grid electricity] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [Captive electricity] For the option a) Specification of the captive power generation system provided by the manufacturer (ηelec,CG [%]). CO2 emission factor of the fossil fuel type used in the captive power generation system (EFfuel,CG [tCO2/GJ]) For the option b) Generated and supplied electricity by the captive power generation system (EGPJ,CG,p [MWh/p]). Fuel amount consumed by the captive power generation system (FCPJ,CG,p [mass or volume/p]). Net calorific value (NCVfuel,CG [GJ/mass or volume]) and CO2 emission factor (EFfuel,CG [tCO2/GJ]) of the fuel consumed by the captive power generation system in order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in tables 1.2 and 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i |  | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| Tchilled-out,i |  | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPRE,i |  | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "MPS (input_separate)"
| COPPJ,i |  | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| COPPJ,tc,i |  | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM11_MRS(input_separate)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
|  | Parameters monitored ex post | Project-specific parameters fixed ex ante | [5 empty] | Ex-post calculation of emissions
Parameters | i | ECPJ,i,p | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of project chiller | Power consumption of project chiller i during the period p | CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Reference emissions of reference chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 0 | 0.9185 | 37 | 7 | 5.69 | 6.22 | 6.22 | 0 | 0 | 0
| 2 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | 0 | 0 | 0

## AM11_MRS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM011_ver01.0
Reference Number: VN011
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## AM12_MPS(input)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project Heat Recovery Electric Heat Pump (HREHP) i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by power meter. A specification of power meter is provided by its manufacturer, and it states that the accuracy stays within ±2.0% being tested in line with JIS C 1111. There is no statement regarding replacement nor calibration interval recommended by the manufacturer. Therefore, power meters are not a subject of calbration nor replacement during the JCM project period. | Continuously | Input on "MPS (input_separate)"
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor for consumed electricity |  | 0.9185 | tCO2/MWh | [Grid electricity] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [Captive electricity] For the option a) Specification of the captive power generation system provided by the manufacturer (ηelec,CG [%]). CO2 emission factor of the fossil fuel type used in the captive power generation system (EFfuel,CG [tCO2/GJ]) For the option b) Generated and supplied electricity by the captive power generation system (EGPJ,CG,p [MWh/p]). Fuel amount consumed by the captive power generation system (FCPJ,CG,p [mass or volume/p]). Net calorific value (NCVfuel,CG [GJ/mass or volume]) and CO2 emission factor (EFfuel,CG [tCO2/GJ]) of the fuel consumed by the captive power generation system in order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in tables 1.2 and 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| EFREreh | CO2 emission factor for the reference equipment for heating energy generation |  | - | tCO2/GJ | [Boiler] In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Electric heater] Same source as the parameter EFelec in this section Note: EFreh=EFelec/3.6 |  |  | Input on "MPS (input_separate)"
| ECRi | Rated electricity consumption of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| ηREh | Efficiency of the reference equipment for heating energy generation |  | - | - | [Boiler] CDM Methodological tool “Determining the baseline efficiency of thermal or electric energy generation systems, Version 2” [Electric heater] Theoretically the most efficient value |  |  | Input on "MPS (input_separate)"
| COPRE,cool,i | COP of reference air-cooled chiller i |  | - | - | The default COP values are derived from the result of survey on COP of air-cooled chillers from manufacturers with high market share. The survey should prove the use of clear methodology. The COPRE,cool should be revised if necessary from survey result which is conducted by JC or project participants. |  |  | Input on "MPS (input_separate)"
| HPJ,i | Rated heating capacity of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
| CHPJ,i | Rated cooling capacity of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "MPS (input_separate)"
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 1116 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM12_MPS(input_separate)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [6 empty] | Ex-ante estimation of emissions
Parameters | i | ECPJ,i,p | EFelec | EFREh | ECRi | ηREh | COPRE,cool,i | HPJ,i | CHPJ,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of project HREHP | Power consumption of project HREHP i during the period p | CO2 emission factor for consumed electricity | CO2 emission factor for the reference equipment for heating energy generation | Rated electricity consumption of project HREHP i | Efficiency of the reference equipment for heating energy generation | COP of reference air-cooled chiller i | Rated heating capacity of project HREHP i | Rated cooling capacity of project HREHP i | Reference emissions of reference electric heater i and air-cooled chiller i during the period p | Project emissions of project HREHP i during the period p | Emissions reductions by the project HREHP i during the period p
Units | - | MWh/p | tCO2/MWh | tCO2/GJ | kW | - | - | kW | kW | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 384 | 0.9185 | 0.25514 | 53.1 | 1 | 3.08 | 180 | 126.9 | 1469.2765 | 352.704 | 1116.5725
| 2 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | 1469.2765 | 352.704 | 1116.5725

## AM12_MPS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 1116.5725 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 1469.2765 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 1469.2765 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 352.704 | tCO2/p | PEp
|  | Project emissions during the period p |  | electricity | 352.704 | tCO2/p | PEp
[List of Default Values]
|  |  | EFelec (For captive electricity) | 0.8 | tCO2/MWh
|  |  | COPRE,cool,i (4≤x≤60USRt) | 3.08 | -
|  |  | COPRE,cool,i (60<x≤140USRt) | 2.96 | -
|  |  | COPRE,cool,i (140<x≤184USRt) | 2.71 | -
|  |  | ηREh (Boiler) | 0.92 | -
|  |  | ηREh (Electric heater) | 1 | -

## AM12_MSS
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| HOYA CORPORATION Environment/Occupational Safety and Health Department Group leader | In charge of authorizing the monitoring report.
| HOYA LENS VIETNAM LTD Technical Expert | In charge of approving the archived data after being checked and corrected when necessary and preparation of monitoring report.
| HOYA LENS VIETNAM LTD Facility Manager | In charge of monitoring procedure (data collection and storage), including monitoring equipments and calibrations, and training of monitoring personnel.
| HOYA LENS VIETNAM LTD Facility Staff | In charge of checking the archived data.

## AM12_MRS(input)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project Heat Recovery Electric Heat Pump (HREHP) i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by power meter. A specification of power meter is provided by its manufacturer, and it states that the accuracy stays within ±2.0% being tested in line with JIS C 1111. There is no statement regarding replacement nor calibration interval recommended by the manufacturer. Therefore, power meters are not a subject of calbration nor replacement during the JCM project period. | Continuously | Input on "MRS (input_separate)"
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | CO2 emission factor for consumed electricity |  | 0.9185 | tCO2/MWh | [Grid electricity] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [Captive electricity] For the option a) Specification of the captive power generation system provided by the manufacturer (ηelec,CG [%]). CO2 emission factor of the fossil fuel type used in the captive power generation system (EFfuel,CG [tCO2/GJ]) For the option b) Generated and supplied electricity by the captive power generation system (EGPJ,CG,p [MWh/p]). Fuel amount consumed by the captive power generation system (FCPJ,CG,p [mass or volume/p]). Net calorific value (NCVfuel,CG [GJ/mass or volume]) and CO2 emission factor (EFfuel,CG [tCO2/GJ]) of the fuel consumed by the captive power generation system in order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in tables 1.2 and 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants. | 0 | 0
| EFREreh |  | CO2 emission factor for the reference equipment for heating energy generation |  | - | tCO2/GJ | [Boiler] In the order of preference: a) value provided by fuel supplier; b) value measured by the project participants; c) regional or national default value; or d) IPCC default value provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Electric heater] Same source as the parameter EFelec in this section Note: EFreh=EFelec/3.6 | 0 | 0 | Input on "MPS (input_separate)"
| ECRi |  | Rated electricity consumption of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer | 0 | 0 | Input on "MPS (input_separate)"
| ηREh |  | Efficiency of the reference equipment for heating energy generation |  | - | - | [Boiler] CDM Methodological tool “Determining the baseline efficiency of thermal or electric energy generation systems, Version 2” [Electric heater] Theoretically the most efficient value | 0 | 0 | Input on "MPS (input_separate)"
| COPRE,cool,i |  | COP of reference air-cooled chiller i |  | - | - | The default COP values are derived from the result of survey on COP of air-cooled chillers from manufacturers with high market share. The survey should prove the use of clear methodology. The COPRE,cool should be revised if necessary from survey result which is conducted by JC or project participants. | 0 | 0 | Input on "MPS (input_separate)"
| HPJ,i |  | Rated heating capacity of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer | 0 | 0 | Input on "MPS (input_separate)"
| CHPJ,i |  | Rated cooling capacity of project HREHP i |  | - | kW | Specifications of project HREHP i prepared for the quotation or factory acceptance test data by manufacturer | 0 | 0 | Input on "MPS (input_separate)"
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipment (Data used: measured values)

## AM12_MRS(input_separate)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
|  | Parameters monitored ex post | Project-specific parameters fixed ex ante | [6 empty] | Ex-post calculation of emissions
Parameters | i | ECPJ,i,p | EFelec | EFREh | ECRi | ηREh | COPRE,cool,i | HPJ,i | CHPJ,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of project HREHP | Power consumption of project HREHP i during the period p | CO2 emission factor for consumed electricity | CO2 emission factor for the reference equipment for heating energy generation | Rated electricity consumption of project HREHP i | Efficiency of the reference equipment for heating energy generation | COP of reference air-cooled chiller i | Rated heating capacity of project HREHP i | Rated cooling capacity of project HREHP i | Reference emissions of reference electric heater i and air-cooled chiller i during the period p | Project emissions of project HREHP i during the period p | Emissions reductions by the project HREHP i during the period p
Units | - | MWh/p | tCO2/MWh | tCO2/GJ | kW | - | - | kW | kW | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 0 | 0.9185 | 0.25514 | 53.1 | 1 | 3.08 | 180 | 126.9 | 0 | 0 | 0
| 2 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 | 0 | 0.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | 0 | 0 | 0

## AM12_MRS(calc_process)
Monitoring Spreadsheet: JCM_VN_AM012_ver01.0
Reference Number: VN011
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | electricity | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | EFelec (For captive electricity) | 0.8 | tCO2/MWh
|  |  | COPRE,cool,i (4≤x≤60USRt) | 3.08 | -
|  |  | COPRE,cool,i (60<x≤140USRt) | 2.96 | -
|  |  | COPRE,cool,i (140<x≤184USRt) | 2.71 | -
|  |  | ηREh (Boiler) | 0.92 | -
|  |  | ηREh (Electric heater) | 1 | -