Joint Crediting Mechanism Approved Methodology VN_AM006

“Introduction of air conditioning system equipped with inverters”

- Title of the methodology

- Introduction of air conditioning system equipped with inverters, Version 01.0

- Terms and definitions

| Terms | Definitions |
| --- | --- |
| Air-conditioning system with inverters | Air-conditioning system with inverters is a type of air conditioning system which contains inverter, an apparatus to control the speed of the compressor motor in line with different load demand. |
| Coefficient of Performance (COP) | Coefficient of Performance (COP) is the cooling capacity per rated electricity consumption of the air conditioning system. The values of cooling capacity and rated electricity consumption are defined under specific temperature stated in ISO5151:2010. In this methodology, a COP value of project air conditioning system is set based on calculation by the value of its cooling capacity divided by the electricity consumption of the outdoor unit according to data by manufacturer. |

- Summary of the methodology

| - Items | - Summary |
| --- | --- |
| - GHG emission reduction measures | This methodology applies to the project that aims for saving energy by introducing air-conditioning system with inverter for cooling in Vietnam. |
| - Calculation of reference emissions | GHG emissions associated with electricity consumption of reference air conditioning system are calculated based on the monitored electricity consumption of project air conditioning system, the ratio of COPs of reference/project air conditioning system, and the CO2 emission factor of the electricity consumed by project air conditioning system. |
| - Calculation of project emissions | - GHG emissions associated with electricity consumption of project air conditioning system are calculated based on the monitored electricity consumption of project air conditioning system and the CO2 emission factor of the electricity consumed by project air conditioning system. |
| - Monitoring parameters | - Electricity consumption of outdoor unit of project air conditioning system - Total electricity consumption of indoor units of project air conditioning system |

- Eligibility criteria

- This methodology is applicable to projects that satisfy all of the following criteria.

| Criterion 1 | Air-conditioning system with inverter is newly installed or installed to replace existing non-inverter air conditioning system. |
| --- | --- |
| Criterion 2 | Cooling capacity of project air conditioning system is more than or equal to 14kW. |
| Criterion 3 | COP of project air-conditioning system has a COP value higher than that of the value indicated in the table below. COP for Reference Air Conditioning System (COPRE,i) Cooling Capacity [kW]; Reference COP. 14 ≤ x < 28; 2.97. 28 ≤ x < 42; 2.94. 42 ≤ x < 56; 2.91. 56 ≤ x; 2.56. |
| Criterion 4 | Ozone Depletion Potential (ODP) of the refrigerant used for project air conditioning system is zero. |
| Criterion 5 | Plans to prevent release of refrigerants into the atmosphere at the time of air conditioning system removal are prepared for both project air conditioning system and the existing air conditioning system replaced by the project. In the case of replacing existing air conditioning system by project air conditioning system, execution of the prevention plan is checked at the time of verification, e.g. re-use of the refrigerant, in order to confirm that refrigerant used for the existing air conditioning system removed by the project is not released to the air. |

- Emission Sources and GHG types

| Reference emissions |  |
| --- | --- |
| Emission sources | GHG types |
| Electricity consumption by reference air conditioning systems | CO2 |
| Project emissions |  |
| Emission sources | GHG types |
| Electricity consumption by project air conditioning systems (include an indoor unit and an outdoor unit) | CO2 |

- Establishment and calculation of reference emissions

F.1. Establishment of reference emissions

Reference emissions are calculated with electricity consumption of project air conditioning system, ratio of COPs of project/reference air conditioning system, and CO2 emission factor for electricity consumed. Taking into consideration the market of air conditioning system in Viet Nam, the COP of reference air conditioning system is conservatively set ex ante in the following manner to ensure the net emission reductions. - The reference COP, at a certain cooling capacity, is set at the maximum value among the COP values of the air conditioning systems of single-split type and non-inverter type, which are currently available in the Vietnamese market, in the respective cooling capacity range.

F.2. Calculation of reference emissions

| REp=iECPJ,i,outdoor,p×COPPJ,i,outdoor÷COPRE,i×EFelec |  |
| --- | --- |
| REp | : Reference emissions during the period p [tCO2/p] |
| ECPJ,i,outdoor,p | : Electricity consumption of outdoor unit of project air conditioning system i during the period p [MWh/p] |
| COPPJ,i,outdoor | : COP of outdoor unit of project air conditioning system i [-] |
| COPRE,i | : COP of reference air conditioning system i [-] |
| EFelec | : CO2 emission factor for consumed electricity [tCO2/MWh] |
| i | : Identification number of air conditioning system [-] |

- Calculation of project emissions

| PEp=iECPJ,i,outdoor,p+ECPJ,indoor,p×EFelec |  |
| --- | --- |
| PEp | : Project emissions during the period p [tCO2/p] |
| ECPJ,i,outdoor,p | : Electricity consumption of outdoor unit of project air conditioning system i during the period p [MWh/p] |
| ECPJ,indoor,p | : Total electricity consumption of indoor units of project air conditioning system during the period p [MWh/p] |
| EFelec | : CO2 emission factor for consumed electricity [tCO2/MWh] |
| i | : Identification number of air conditioning system [-] |

- Calculation of emissions reductions

| ERp = REp - PEp |  |
| --- | --- |
| ERp | : Emissions reductions during the period p [tCO2/p] |
| REp | : Reference emissions during the period p [tCO2/p] |
| PEp | : Project emissions during the period p [tCO2/p] |

- Data and parameters fixed ex ante

The source of each data and parameter fixed ex ante is listed as below.

| Parameter | Description of data | Source |
| --- | --- | --- |
| EFelec | CO2 emission factor for consumed electricity. When captive power generation is not available at the project site, then the most recent Vietnamese national grid emission factor [EFgrid] available at the time of validation is applied as [EFelec] and fixed for the monitoring period thereafter. When captive power generation is available at the project site, then [EFelec] is conservatively selected as below and fixed for the monitoring period thereafter: EFelec = min(EFgrid, EFcaptive) EFcaptive = 0.8 tCO2/MWh* *The most recent emission factor available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. | [EFgrid] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology: AMS-I.A |
| COPRE,i | COP of reference air conditioning system i, as indicated in Table 1. The values of cooling capacity and rated electricity consumption used in the calculation of COP are obtained from product catalogs, specification documents or website, hearing survey of major manufacturers in Vietnam. Table 1 : COP for Reference Air Conditioning System (COPRE,i) Cooling Capacity [kW]; Reference COP. 14 ≤ x < 28; 2.97. 28 ≤ x < 42; 2.94. 42 ≤ x < 56; 2.91. 56 ≤ x; 2.56. | Nominal value available on product catalogs, specification documents or websites, hearing survey. The default values are derived from the result of survey on COP of air conditioning system with non-inverter from manufacturers that have high market share. The default values should be revised if necessary from survey result which is conducted by JC or project participants every three years. The survey should prove the use of clear methodology. |
| COPPJ,i,outdoor | COP of outdoor unit of project air conditioning system i. The COP is calculated by using the value of cooling capacity and rated electricity consumption of outdoor unit provided by manufacturer. | Specifications of project air conditioning system for the quotation or factory acceptance test data by manufacturer. |

History of the document

| Version | Date | Contents revised |
| --- | --- | --- |
| 01.0 | 20 October 2016 | JC5, Annex 7 Initial approval. |