## PMS(input)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously | Input on "PMS (input_separate)"
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | CO2 emission factor for consumed electricity |  | 0 | tCO2/MWh | [Grid electricity] Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee. [Captive electricity] For the option a) Specification of the captive power generation system provided by the manufacturer (ηelec,CG [%]). CO2 emission factor of the fossil fuel type used in the captive power generation system (EFfuel,CG [tCO2/GJ]) For the option b) Generated and supplied electricity by the captive power generation system (EGPJ,CG,p [MWh/p]). Fuel amount consumed by the captive power generation system (FCPJ,CG,p [mass or volume/p]). Net calorific value (NCVfuel,CG [GJ/mass or volume]) and CO2 emission factor (EFfuel,CG [tCO2/GJ]) of the fuel consumed by the captive power generation system in order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in tables 1.2 and 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "PMS (input_separate)"
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "PMS (input_separate)"
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology |  |  | Input on "PMS (input_separate)"
| COPPJ,i | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer |  |  | Input on "PMS (input_separate)"
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## PMS(input_separate)
JCM_VN_F_PMS_ver02.0
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [5 empty] | Ex-ante estimation of emissions
Parameters | i | ECPJ,i,p | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | REi,p | PEi,p | ERi,p
Description of data | Identification number of project chiller | Power consumption of project chiller i during the period p | CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific condition | Output chilled water temperature of project chiller i set under the project specific condition | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Reference emissions of reference chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0 | 0 | 0
| Total | - | - |  |  |  | - | - | 0 | 0 | 0

## PMS(calc_process)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (300≤x<450USRt) | 5.59 | -
|  |  | COPRE,i (450≤x<550USRt) | 5.69 | -
|  |  | COPRE,i (550≤x<825USRt) | 5.85 | -
|  |  | COPRE,i (825≤x≤1,500USRt) | 6.06 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius