## PMS(input)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | - | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously
| (2) | FCPJ,CG,p | Amount of fuel input for captive power generation during monitoring period p |  | mass or volume/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company for option(b). | Continuously
| (3) | EGPJ,CG,p | Amount of electricity generated by captive power generation system during the period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. If the amount of electricity generated by renewable energy sources estimated from their generation capacities is more than half of the total electricity consumption at the project site, total amount of electricity generated by both fossil fuel and renewable sources is input for EGPJ,CG,p. Otherwise, the amount of electricity generated by only fossil fuel is input for EGPJ,CG,p. | Continuously
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | [For grid electricity] CO2 emission factor for consumed electricity |  |  | tCO2/MWh | Ministry of Natural Resources and Environment of Vietnam (MONRE), Vietnamese DNA for CDM unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  |  | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version02.0" for the default efficiency for off-grid power plants.
| ηelec,CG | [For captive electricity, Option a] Power generation efficiency |  |  | % | The power generation efficiency based on lower heating value (LHV) of the captive power generation system from the manufacturer’s specification
| EFfuel,CG | [For captive electricity] CO2 emission factor of the fuel consumed by the captive power generation system |  |  | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| NCVfuel,CG | [For captive electricity, Option b] Net calorific value of fuel consumed by the captive power generation system |  |  | GJ/mass or volume | the amount of electricity generated by renewable energy sources estimated from their generation capacities is more than half, the CO2 emission factor is determined by option (b) 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific conditions |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific conditions |  | - | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | - | - | Selected from the default values set in the methodology
| COPPJ,i | COP of project chiller i under the project specific conditions |  | - | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | - | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(input_separate)
JCM_VN_F_PMS_ver02.0
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante | [8 empty] | Ex-ante estimation of emissions
Parameters | Chiller i | ECPJ,i,p | EFelec | EFelec | EFelec | EFelec | Tcooling-out,i | Tchilled-out,i | COPRE,i | COPPJ,i | COPPJ,tc,i | REi,p | PEi,p | ERi,p
Description of data | Project chiller No. | Power consumption of project chiller i during the period p | [For grid electricity] CO2 emission factor for consumed electricity | [For captive electricity] CO2 emission factor for consumed electricity Option a | [For captive electricity] CO2 emission factor for consumed electricity Option b | [For captive electricity] CO2 emission factor for consumed electricity | Output cooling water temperature of project chiller i set under the project specific conditions | Output chilled water temperature of project chiller i set under the project specific conditions | COP of reference chiller i under the standardizing temperature conditions | COP of project chiller i under the project specific conditions | COP of project chiller i calculated under the standardizing temperature conditions | Reference emissions of project chiller i during the period p | Project emissions of project chiller i during the period p | Emissions reductions by the project chiller i during the period p
Units | - | MWh/p | tCO2/MWh | tCO2/MWh | tCO2/MWh | tCO2/MWh | degree Celsius | degree Celsius | - | - | - | tCO2/p | tCO2/p | tCO2/p
Estimated values | 1 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 2 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 3 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 4 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 5 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 6 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 7 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 8 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 9 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 10 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 11 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 12 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 13 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 14 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 15 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 16 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 17 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 18 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 19 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 20 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| Total | - | - | - | - | - | - | - | - | - | - | 0 | 0 | 0

## PMS(calc_process)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Reference emissions during the period p |  | N/A | 0 | tCO2/p | REp
3. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Project emissions during the period p |  | N/A | 0 | tCO2/p | PEp
[List of Default Values]
|  |  | COPRE,i (300<=x<=700 USRt) | 5.67 | -
|  |  | COPRE,i (700<x<=1,100 USRt) | 5.87 | -
|  |  | COPRE,i (1,100<x<=1,500 USRt) | 6.05 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius