## PMS(input)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ESelec,p | Amount of electricity (generated by project biomass cogeneration system) supplied to the recipient facility during the period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously
| (2) | SSPJ,p | Amount of steam (generated by project biomass cogeneration system) supplied to the recipient facility during the period p |  | t/p | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously
| (3) | Tfw,p | Temperature of feed water into biomass boiler(s) of project biomass cogeneration system during the period p |  | degree Celsius | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. In case that the parameter is measured as a unit of cubic meter (m3) by measuring equipment, 1.0 t/m3 is applied to the density of water for simplification. | Continuously | In case that Tfw,p is monitored
| (4) | Tdw,p | Temperature of drain recovery water reused by biomass boiler(s) of project biomass cogeneration system during the period p |  | degree Celsius | Option C | Monitored data | Data is measured by measuring equipment in the factory. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously | In case that Tfw,p is not monitored
| (5) | FCPJ,i,p | Amount of auxiliary fossil fuel consumption at the start-up by biomass boiler(s) of project biomass cogeneration system for the fuel type i during the period p | - | mass or volume/p | Option B or Option C | Invoice from fuel supply company or monitored data | Data is measured by measuring equipment in the factory. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipment. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously
| (6) | Dj,p | Round trip distance of the biomass transportation j during the period p | - | km | Option A or Option C | Map information or monitored data | Data is collected from map information or measured by measuring equipment in vehicles. Recorded data is checked its integrity once a month by responsible staff. | Once for each transportation | Input on "MPS (input_separate)"
| (7) | mj,p | Mass of biomass transported in the biomass transportation j during the period p | - | t/p | Option B or Option C | Invoice from fuel supply company or monitored data | Data is collected and recorded from the invoices by the fuel supply company, or data is measured by measuring equipment in the factory. Recorded data is checked its integrity once a month by responsible staff. | Once for each transportation | Input on "MPS (input_separate)"
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec,RE | Reference CO2 emission factor for the displaced electricity system |  |  | tCO2/MWh | The value for EFelec,RE is selected from the emission factor based on the national grid (EFRE,grid) or based on captive diesel power generator (EFRE,cap) in the following manners: In case the displaced electricity system in a project activity is connected to the national grid including through internal grid which is not connected to a captive power generator, EFRE,grid, 0.333 tCO2/MWh is applied. In case the displaced electricity system in a project activity is connected to an internal grid which is connected to both the national grid and a captive power generator, EFRE,grid, 0.333 tCO2/MWh is applied. In case the PV system in a project activity is connected to an internal grid which is not connected to the national grid, EFRE,cap, 0.533 tCO2/MWh is applied. The default emission factor is derived from the result of the survey on the generation efficiency of major natural gas-fired power plants in Viet Nam and the default heat efficiency of 49% which is set above the value of the most efficient diesel power generator. The default value is revised if deemed necessary by the JC.
| h''steam | Specific enthalpy of supplied steam |  |  | MJ/t | Saturated steam table based on “IAPWS Industrial Formulation” (e.g. steam table published by The Japan Society of Mechanical Engineers), using the values for setting steam pressure according to vendor specification, contract condition by the steam buyer or operation manual on the site. If there is a case that actual operated record of the parameter is lower than the ex ante value of the one, the fixed ex ante value is changed into the lowest one of actual operated records during the monitoring period.
| Cp | Specific heat capacity of water |  | 4.184 | MJ/(t·Δ°C) | A default value is set to 4.184 [MJ/(t·Δ°C)] Theoretical value provided in table 6 of Cabinet Order No. 357 of 1992, Japan
| ηRE | Reference boiler efficiency |  | 0.92 | dimensionless | The default value is set to 92% according to “Natural gas without condenser” in table 1 (Default efficiency factor for thermal applications) of CDM Methodological tool 09 “Determining the baseline efficiency of thermal or electric energy generation systems” Version 03.0
| EFfuel,RE | CO2 emission factor for fossil fuel consumed by the reference boiler |  |  | tCO2/GJ | CO2 emission factor of natural gas is applied in this methodology in a conservative manner. In order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| NCVfuel,PJ,i | Net calorific value of auxiliary fossil fuel used by biomass boiler(s) of project biomass cogeneration system for the fuel type i |  |  | GJ/mass or volume | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFfuel,PJ,i | CO2 emission factor of auxiliary fossil fuel used by biomass boiler(s) of project biomass cogeneration system for the fuel type i |  |  | tCO2/GJ | In the order of preference: a) values provided by fuel supplier; b) measurement by the project participants; c) regional or national default values; or d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Upper value is applied.
| EFtr | CO2 emission factor for biomass transportation |  | - | tCO2/t·km | CDM methodological tool “TOOL 12: Project and leakage emissions from transportation of freight, version 01.1. Light vehicles: Vehicles with a gross vehicle mass being less or equal to 26 tonnes. Heavy vehicles: Vehicles with a gross vehicle mass being higher than 26 tonnes. * If both vehicle classes are used in the project, the higher value (0.000245 tCO2/t·km) is applied. ** If biomass is transported by river boat, the higher value (0.000129 tCO2/t·km)) is applied in conservative manner. According to a lot of materials by Ministry of Land, Infrastructure, Transport and Tourism, Japan (MLITJ), CO2 emission intensity by ship (including on river) is much lower than the one by truck transportation. |  |  | Input on "PMS (input_separate)"
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipment (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipment (Data used: measured values)

## PMS(input_separate)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Input Sheet) [Attachment to Proposed Methodology Form]
Table 4-1: Parameters for calculation of project emissions from combustion of fossil fuel by the project boiler(s)
|  | Parameters to be monitored ex post | Project-specific parameters to be fixed ex ante |  | Ex-ante estimation of emissions
Description of data | i | FCPJ,i,p | NCVfuel,PJ,i | EFfuel,PJ,i | PEfuel,p
Parameters | Identification number of fossil fuel type | Amount of auxiliary fossil fuel consumption at the start-up by biomass boiler(s) of project biomass cogeneration system for the fuel type i during the period p | Net calorific value of auxiliary fossil fuel used by biomass boiler(s) of project biomass cogeneration system for the fuel type i | CO2 emission factor of auxiliary fossil fuel used by biomass boiler(s) of project biomass cogeneration system for the fuel type i | Project emissions from combustion of fossil fuel by the project boiler(s) of project biomass cogeneration system during the period p
Units | - | mass or volume/p | GJ/mass or volume | tCO2/GJ | tCO2/p
Estimated value |  |  |  |  | 0
0
0
0
0
| Total | - | - |  | 0
Table 4-2: Parameters for calculation of project emissions from biomass transportation
|  | Parameters to be monitored ex post |  | Parameters to be fixed ex ante | Ex-ante estimation of emissions
Parameters | j | Dj,p | mj,p | EFtr | PEtr,p
Description of data | Identification number of the round trip for biomass transportation between the place of biomass supplier’s stockyard and the project site | Round trip distance of the biomass transportation j during the period p | Mass of biomass transported in the biomass transportation j during the period p | CO2 emission factor for biomass transportation | Project emissions from biomass transportation during the period p
Units | - | km | t/p | tCO2/t·km | tCO2/p
Estimated value | 1 |  |  |  | 0
| 2 |  |  |  | 0
| 3 |  |  |  | 0
| 4 |  |  |  | 0
| 5 |  |  |  | 0
| 6 |  |  |  | 0
| 7 |  |  |  | 0
| 8 |  |  |  | 0
| 9 |  |  |  | 0
| 10 |  |  |  | 0
| 11 |  |  |  | 0
| 12 |  |  |  | 0
| 13 |  |  |  | 0
| 14 |  |  |  | 0
| 15 |  |  |  | 0
| 16 |  |  |  | 0
| 17 |  |  |  | 0
| 18 |  |  |  | 0
| 19 |  |  |  | 0
| 20 |  |  |  | 0
| 21 |  |  |  | 0
| 22 |  |  |  | 0
| 23 |  |  |  | 0
| 24 |  |  |  | 0
| 25 |  |  |  | 0
| 26 |  |  |  | 0
| 27 |  |  |  | 0
| 28 |  |  |  | 0
| 29 |  |  |  | 0
| 30 |  |  |  | 0
| 31 |  |  |  | 0
| 32 |  |  |  | 0
| 33 |  |  |  | 0
| 34 |  |  |  | 0
| 35 |  |  |  | 0
| 36 |  |  |  | 0
| 37 |  |  |  | 0
| 38 |  |  |  | 0
| 39 |  |  |  | 0
| 40 |  |  |  | 0
| 41 |  |  |  | 0
| 42 |  |  |  | 0
| 43 |  |  |  | 0
| 44 |  |  |  | 0
| 45 |  |  |  | 0
| 46 |  |  |  | 0
| 47 |  |  |  | 0
| 48 |  |  |  | 0
| 49 |  |  |  | 0
| 50 |  |  |  | 0
| Total |  |  |  | 0

## PMS(calc_process)
JCM_VN_F_PMS_ver02.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | 0 | tCO2/p | ERp
2. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | 0 | tCO2/p | REp
|  | Reference emissions for electricity supply during the period p |  | N/A | 0 | tCO2/p | REelec,p
|  | Reference emissions for heat supply during the period p |  | Natural gas | 0 | tCO2/p | REheat,p
3. Calculations of the project emissions
| Project emissions during the period p |  |  |  | 0 | tCO2/p | PEp
|  | Project emissions from combustion of fossil fuel by biomass boiler(s) of project biomass cogeneration system during the period p |  | N/A | 0 | tCO2/p | PEfuel,p
|  | Project emissions from biomass transportation during the period p |  | N/A | 0 | tCO2/p | PEtr,p
[List of Default Values]
ηRE
|  |  | Reference boiler efficiency | 0.92 | -
EFfuel,RE
|  |  | CO2 emission factor of natural gas | 0.0543 | tCO2/GJ
NCVfuel,PJ,i
|  |  | Net calorific value of Natural gas | 50.4 | GJ/t
|  |  | Net calorific value of Natural Gas Liquids | 46.9 | GJ/t
|  |  | Net calorific value Liquefied Petroleum Gases | 52.2 | GJ/t
|  |  | Net calorific value of Diesel Oil | 43.3 | GJ/t
|  |  | Net calorific value of Residual Fuel Oil | 41.7 | GJ/t
|  |  | Net calorific value of Sub-Bituminous Coal | 26 | GJ/t
|  |  | Net calorific value of other Bituminous Coal | 30.5 | GJ/t
|  |  | Net calorific value of Lignite | 21.6 | GJ/t
EFfuel,PJ,i
|  |  | CO2 emission factor of Natural gas | 0.0583 | tCO2/GJ
|  |  | CO2 emission factor of Natural Gas Liquids | 0.0704 | tCO2/GJ
|  |  | CO2 emission factor of Liquefied Petroleum Gases | 0.0656 | tCO2/GJ
|  |  | CO2 emission factor of Diesel Oil | 0.0748 | tCO2/GJ
|  |  | CO2 emission factor of Residual Fuel Oil | 0.0788 | tCO2/GJ
|  |  | CO2 emission factor of Sub-Bituminous Coal | 0.1 | tCO2/GJ
|  |  | CO2 emission factor of other Bituminous Coal | 0.0997 | tCO2/GJ
|  |  | CO2 emission factor of Lignite | 0.115 | tCO2/GJ
|  |  | CO2 emission factor for biomass transportation trip | EFtr
|  |  | Light vehicle | 0.000245 | tCO2/t·km
|  |  | Heavy vehicle | 0.000129 | tCO2/t·km