## MPS(input)
Monitoring Spreadsheet: JCM_BD_AM001_ver02.0
Reference Number: BD001
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECPJ,i,p | Power consumption of project chiller i during the period p | 1338.1 | MWh/p | Option C | Monitored data | Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Electrical power meter is applied for measurement of electrical power consumption of project chiller. 2) Meter is certified in compliance with IEC 62053-23 class 2. - Measuring and recording: 1) Measured data is recorded and stored in the measuring equipments with manufacture's specification within ±5% accuracy level which is required as the instrument error in Joint Crediting Mechanism Guidelines for Developing Project Design Document and Monitoring Report. 2) Recorded and compiled data is checked its integrity once a month with monitoring manual by responsible staff. - Calibration: The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Continuously
| (2) | FCPJ,p | The amount of fuel input for power generation during the monitoring period p |  | mass or volume/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company. | Continuously | for option b)
| (3) | EGPJ,p | The amount of electricity generated during the monitoring period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously | for option b)
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec | [For grid electricity] CO2 emission factor for consumed electricity |  |  | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Bangladesh”, endorsed by National CDM Committee unless otherwise instructed by the Joint Committee.
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated. |  |  | Calculated
| EFelec | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | 0.46 | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version 02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i | Output cooling water temperature of project chiller i set under the project specific condition |  | 36.9 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| Tchilled-out,i | Output chilled water temperature of project chiller i set under the project specific condition |  | 7 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPRE,i | COP of reference chiller i under the standardizing temperature conditions |  | 5.13 | - | Selected from the default values set in the methodology
| COPPJ,i | COP of project chiller i under the project specific conditions |  | 6.0469 | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPPJ,tc,i | COP of project chiller i calculated under the standardizing temperature conditions |  | 6.0286 | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec | Power generation efficiency |  |  | % | Specification of the captive power generation system provided by the manufacturer. |  |  | for option a)
| NCVfuel | Net calorific value of consumed fuel |  |  | GJ/mass or volume | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | for option b)
| EFfuel | CO2 emission factor of consumed fuel |  |  | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | for both option a) and b)
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 107 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)
Monitoring Spreadsheet: JCM_BD_AM001_ver02.0
Reference Number: BD001
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 107.8132 | tCO2/p | ERp
2. Selected default values, etc.
| COP of reference chiller i under the standardizing temperature conditions |  |  | N/A | 5.13 | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 723.3392 | tCO2/p | REp
|  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity with lower value [grid or captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | Power consumption of project chiller i |  | Electricity | 1338.1 | MWh/p | ECPJ,i,p
|  | COP of reference chiller i under the standardizing temperature conditions |  | N/A | 5.13 | - | COPRE,i
|  | COP of project chiller i calculated under the standardizing temperature conditions |  | N/A | 6.0286 | - | COPPJ,tc,i
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 615.526 | tCO2/p | PEp
|  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity with lower value [grid or captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | Power consumption of project chiller i |  | Electricity | 1338.1 | MWh/p | ECPJ,i,p
[List of Default Values]
|  |  | COPRE,i (x<300USRt) | 5.13 | -
|  |  | COPRE,i (300≤x<700USRt) | 5.5 | -
|  |  | COPRE,i (700≤x<1,150USRt) | 5.66 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius

## MSS
Monitoring Spreadsheet: JCM_BD_AM001_ver02.0
Reference Number: BD001
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Plant Director (technical) | To approve the monitored data. To keep and archive monitored and required data in the verification and issuance for two years after the final issuance of credits
| Chiller operator | To compile and report the chiller data to plant director Daily maintenance

## MRS(input)
Monitoring Spreadsheet: JCM_BD_AM001_ver02.0
Reference Number: BD001
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECPJ,i,p | Power consumption of project chiller i during the period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously
|  | (2) | FCPJ,p | The amount of fuel input for power generation during the monitoring period p |  | mass or volume/p | Option B | Invoice from fuel supply company | Data is collected and recorded from the invoices by the fuel supply company. | Continuously | for option b)
|  | (3) | EGPJ,p | The amount of electricity generated during the monitoring period p |  | MWh/p | Option C | Monitored data | Data is measured by measuring equipment. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Continuously | for option b)
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| EFelec |  | [For grid electricity] CO2 emission factor for consumed electricity |  | 0 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Grid Emission Factor (GEF) of Bangladesh”, endorsed by National CDM Committee unless otherwise instructed by the Joint Committee.
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option a |  | 0 | tCO2/MWh | Power generation efficiency obtained from manufacturer's specification |  |  | Calculated
| EFelec |  | [For captive electricity] CO2 emission factor for consumed electricity Option b |  | 0 | tCO2/MWh | The power generation efficiency calculated from monitored data of the amount of fuel input for power generation and the amount of electricity generated. |  |  | Calculated
| EFelec |  | [For captive electricity] In case the captive electricity generation system meets all of the following conditions; - The system is non-renewable generation system - Electricity generation capacity of the system is less than or equal to 15 MW |  | 0.46 | tCO2/MWh | [Captive electricity with diesel fuel] CDM approved small scale methodology: AMS-I.A. [Captive electricity with natural gas] 2006 IPCC Guidelines on National GHG Inventories for the source of EF of natural gas. CDM Methodological tool "Determining the baseline efficiency of thermal or electric energy generation systems version 02.0" for the default efficiency for off-grid power plants.
| Tcooling-out,i |  | Output cooling water temperature of project chiller i set under the project specific condition |  | 36.9 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| Tchilled-out,i |  | Output chilled water temperature of project chiller i set under the project specific condition |  | 7 | degree Celsius | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPRE,i |  | COP of reference chiller i under the standardizing temperature conditions |  | 5.13 | - | Selected from the default values set in the methodology
| COPPJ,i |  | COP of project chiller i under the project specific conditions |  | 6.0469 | - | Specifications of project chiller i prepared for the quotation or factory acceptance test data by manufacturer
| COPPJ,tc,i |  | COP of project chiller i calculated under the standardizing temperature conditions |  | 6.0286 | - | Calculated with the following equation; COPPJ,tc,i= COPPJ,i × [(Tcooling-out,i - Tchilled-out,i + TDchilled + TDcooling) ÷ (37 - 7 + TDchilled + TDcooling)]
| ηelec |  | Power generation efficiency |  | 0 | % | Specification of the captive power generation system provided by the manufacturer. |  |  | for option a)
| NCVfuel |  | Net calorific value of consumed fuel |  | 0 | GJ/mass or volume | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | for option b)
| EFfuel |  | CO2 emission factor of consumed fuel |  | 0 | tCO2/GJ | In order of preference: 1) values provided by the fuel supplier; 2) measurement by the project participants; 3) regional or national default values; 4) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | for both option a) and b)
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_BD_AM001_ver02.0
Reference Number: BD001
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| COP of reference chiller i under the standardizing temperature conditions |  |  | N/A | 5.13 | - | COPRE,i
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity with lower value [grid or captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | Power consumption of project chiller i |  | Electricity | 0 | MWh/p | ECPJ,i,p
|  | COP of reference chiller i under the standardizing temperature conditions |  | N/A | 5.13 | - | COPRE,i
|  | COP of project chiller i calculated under the standardizing temperature conditions |  | N/A | 6.0286 | - | COPPJ,tc,i
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | CO2 emission factor for consumed electricity [grid] |  | Electricity | 0 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity [captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | CO2 emission factor for consumed electricity with lower value [grid or captive] |  | Electricity | 0.46 | tCO2/MWh | EFelec
|  | Power consumption of project chiller i |  | Electricity | 0 | MWh/p | ECPJ,i,p
[List of Default Values]
|  |  | COPRE,i (x<300USRt) | 5.13 | -
|  |  | COPRE,i (300≤x<700USRt) | 5.5 | -
|  |  | COPRE,i (700≤x<1,150USRt) | 5.66 | -
|  |  | TDcooling | 1.5 | degree Celsius
|  |  | TDchilled | 1.5 | degree Celsius